## 1
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-01-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr) | S-SUP | R-S
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | 90.7407 | 78.0488
Friday | 2010-01-01 | 9:30:am | 12 | 4.4 | 333 | 7.3 | 2.5 | 345 | 9 | 339 | 7.4 | 27 | 335 | 21 | 342 | 7.5 | 123 | 348 | 66 | 2400 | 49 | 13000 | 88.2609 | 82.0312
|  | 11:30:am | 13 | 4.2 | 337 | 7.4 | 2.7 | 351 | 7 | 342 | 7.6 | 23 | 344 | 17 | 347 | 7.6 | 128 | 352 | 57 |  |  |  | 88.5714 | 84.2105
|  | 1:30:pm | 14 | 4 | 339 | 7.4 | 2.4 | 355 | 5 | 345 | 7.5 | 21 | 349 | 15 | 351 | 7.6 | 133 | 363 | 53 |  |  |  | 88 | 89.1775
Saturday | 2010-01-02 | 9:30:am | 13 | 4.9 | 335 | 7.4 | 3 | 352 | 11 | 339 | 7.5 | 25 | 355 | 22 | 342 | 7.6 | 231 | 362 | 59 | 4000 | 48 | 13000 | 87.1429 | 90.0474
|  | 11:30:am | 14 | 4.5 | 337 | 7.5 | 2.7 | 358 | 13 | 345 | 7.6 | 21 | 361 | 18 | 345 | 7.7 | 211 | 373 | 51 |  |  |  | 86.1111 | 90.8629
|  | 1:30:pm | 15 | 4.1 | 342 | 7.5 | 2.5 | 361 | 10 | 349 | 76 | 18 | 365 | 13 | 348 | 7.7 | 197 | 379 | 45 |  |  |  | 94.8795 | 71.1304
Sunday | 2010-01-03 | 9:30:am | 13 | 5 | 332 | 7.3 | 1.7 | 433 | 8 | 336 | 7.4 | 33.2 | 200 | 46 | 345 | 7.6 | 115 | 255 | 44 | 2550 | 45 | 13000 | 94.7368 | 76.8293
|  | 11:30:am | 14 | 4.7 | 338 | 7.4 | 1.5 | 421 | 6 | 339 | 7.5 | 28.5 | 224 | 38 | 349 | 7.7 | 123 | 271 | 42 |  |  |  | 92.3077 | 80.5512
|  | 1:30:pm | 15 | 4.3 | 345 | 7.5 | 1.9 | 417 | 5 | 347 | 7.6 | 24.7 | 231 | 33 | 356 | 7.8 | 127 | 277 | 36 |  |  |  | 86.1671 | 82.2051
Monday | 2010-01-04 | 9:30:am | 12 | 5 | 339 | 7.4 | 4.8 | 300 | 4.4 | 345 | 7.5 | 34.7 | 133 | 30 | 349 | 7.6 | 195 | 466 | 150 | 3750 | 49 | 11000 | 87.3817 | 84.4608
|  | 11:30:am | 13 | 4.7 | 342 | 7.5 | 4 | 315 | 6.8 | 349 | 7.6 | 31.7 | 154 | 26 | 356 | 7.7 | 204 | 435 | 123 |  |  |  | 88 | 87.0892
|  | 1:30:pm | 14 | 4.2 | 349 | 7.5 | 3.3 | 323 | 8.3 | 353 | 7.6 | 27.5 | 166 | 22 | 361 | 7.8 | 213 | 423 | 115 |  |  |  | 83.1081 | 82.1687
Tuesday | 2010-01-05 | 9:30:am | 12 | 4.8 | 339 | 7.3 | 5 | 700 | 13 | 343 | 7.4 | 29.6 | 766 | 34 | 349 | 7.6 | 166 | 388 | 88 | 3000 | 52 | 11000 | 81.8182 | 85.0296
|  | 11:30:am | 13 | 4.4 | 345 | 7.4 | 4.6 | 659 | 15 | 348 | 7.5 | 25.3 | 745 | 31 | 355 | 7.7 | 169 | 383 | 76 |  |  |  | 81.8565 | 85.2795
|  | 1:30:pm | 14 | 4 | 349 | 7.5 | 4.3 | 635 | 12 | 352 | 7.6 | 23.7 | 740 | 27 | 363 | 7.7 | 161 | 397 | 72 |  |  |  | 82.6087 | 85.1613
Wednesday | 2010-01-06 | 9:30:am | 13 | 4.5 | 345 | 7.5 | 4 | 500 | 14 | 349 | 7.6 | 23 | 512 | 27 | 354 | 7.8 | 155 | 394 | 93 | 2550 | 50 | 11000 | 82.381 | 85.8108
|  | 11:30:am | 14 | 4.1 | 351 | 7.6 | 3.7 | 512 | 11 | 353 | 7.6 | 21 | 523 | 23 | 359 | 7.8 | 148 | 399 | 85 |  |  |  | 83.5 | 85.9155
|  | 1:30:pm | 15 | 4 | 355 | 7.6 | 3.3 | 523 | 10 | 356 | 7.7 | 20 | 529 | 20 | 363 | 7.8 | 142 | 393 | 79 |  |  |  | 88.7133 | 62.4576
Thursday | 2010-01-07 | 9:30:am | 13 | 5 | 343 | 7.5 | 5 | 346 | 13 | 348 | 7.6 | 44.3 | 349 | 28 | 353 | 7.8 | 118 | 378 | 45 | 2500 | 48 | 11000 | 89.7129 | 66.8254
|  | 11:30:am | 14 | 4.6 | 349 | 7.6 | 4.3 | 355 | 11 | 353 | 7.7 | 41.8 | 355 | 25 | 359 | 7.8 | 126 | 384 | 49 |  |  |  | 89.011 | 70.88
|  | 1:30:pm | 15 | 4.2 | 352 | 7.6 | 4 | 362 | 10 | 358 | 7.7 | 36.4 | 363 | 21 | 366 | 7.8 | 125 | 399 | 55 |  |  |  | 85.7143 | 67.6923
Friday | 2010-01-08 | 9:30:am | 15 | 4.5 | 357 | 7.3 | 3 | 133 | 13 | 361 | 7.4 | 21 | 376 | 23 | 365 | 7.5 | 65 | 387 | 57 | 1050 | 45 | 11000 | 89.9135 | 67.6923
|  | 11:30:am | 16 | 4.2 | 359 | 7.4 | 3.5 | 145 | 11 | 365 | 7.5 | 34.7 | 365 | 25 | 368 | 7.6 | 69 | 389 | 52 |  |  |  | 86.5942 | 55.4839
|  | 1:30:pm | 17 | 4 | 363 | 7.4 | 3.7 | 155 | 9 | 366 | 7.6 | 27.6 | 362 | 27 | 373 | 7.7 | 62 | 394 | 47 |  |  |  | 91.0072 | 64.359
Saturday | 2010-01-09 | 9:30:am | 15 | 4.3 | 353 | 7.4 | 2.5 | 234 | 15 | 355 | 7.5 | 27.8 | 365 | 21 | 359 | 7.6 | 78 | 392 | 49 | 900 | 48 | 11000 | 85.7143 | 66.9444
|  | 11:30:am | 16 | 4 | 356 | 7.5 | 3.4 | 255 | 12 | 359 | 7.6 | 23.8 | 361 | 18 | 366 | 7.7 | 72 | 395 | 41 |  |  |  | 73.913 | 81.746
|  | 1:30:pm | 17 | 4 | 358 | 7.6 | 3 | 261 | 11 | 366 | 7.7 | 11.5 | 358 | 16 | 371 | 7.8 | 63 | 399 | 39 |  |  |  | 84.8624 | 81.746
Sunday | 2010-01-10 | 9:30:am | 14 | 4 | 351 | 7.5 | 3.3 | 133 | 10 | 355 | 7.6 | 21.8 | 386 | 33.6 | 362 | 7.7 | 53 | 400 | 53.9 | 1050 | 44 | 11000 | 83.9572 | 61.0417
|  | 11:30:am | 15 | 4 | 353 | 7.5 | 3 | 141 | 7 | 358 | 7.7 | 18.7 | 376 | 27.5 | 367 | 7.8 | 48 | 411 | 47.8 |  |  |  | 77.5 | 71.4286
|  | 1:30:pm | 16 | 4 | 355 | 7.6 | 2.7 | 148 | 8 | 362 | 7.7 | 12 | 364 | 24.7 | 374 | 7.8 | 42 | 421 | 41.7 |  |  |  | 81.6327 | 60.6426
Monday | 2010-01-11 | 9:30:am | 13 | 4.5 | 351 | 7.3 | 3.6 | 233 | 2.4 | 355 | 7.4 | 19.6 | 286 | 29.2 | 359 | 7.6 | 49.8 | 266 | 39.2 | 1050 | 41 | 11000 | 81.7073 | 60.5769
|  | 11:30:am | 14 | 4 | 348 | 7.4 | 3 | 242 | 3.7 | 352 | 7.5 | 16.4 | 281 | 24.7 | 355 | 7.7 | 41.6 | 269 | 34.2 |  |  |  | 83.5526 | 65.2968
|  | 1:30:pm | 16 | 4 | 345 | 7.5 | 2.5 | 248 | 5.8 | 348 | 7.6 | 15.2 | 275 | 22.2 | 353 | 7.7 | 43.8 | 274 | 27.4 |  |  |  | 89.7368 | 72.4638
Tuesday | 2010-01-12 | 9:30:am | 14 | 4 | 353 | 7.4 | 3.9 | 344 | 11 | 355 | 7.5 | 38 | 321 | 34 | 359 | 7.6 | 138 | 345 | 48 | 2700 | 48 | 11000 | 92.3077 | 72.9167
|  | 11:30:am | 15 | 4 | 355 | 7.5 | 3 | 351 | 9 | 359 | 7.6 | 39 | 324 | 31 | 363 | 7.7 | 144 | 353 | 55 |  |  |  | 90 | 78.2895
|  | 1:30:pm | 16 | 4 | 358 | 7.5 | 3.3 | 359 | 7 | 363 | 7.6 | 33 | 329 | 27 | 366 | 7.7 | 152 | 359 | 57 |  |  |  | 86.3636 | 67.4074
Wednesday | 2010-01-13 | 9:30:am | 12 | 4.9 | 355 | 7.4 | 3.6 | 400 | 10 | 358 | 7.5 | 26.4 | 412 | 34.8 | 362 | 7.7 | 81 | 455 | 80.8 | 1800 | 44 | 11000 | 87.7119 | 73.1818
|  | 11:30:am | 13 | 4.5 | 358 | 7.5 | 2.9 | 396 | 7 | 362 | 7.6 | 23.6 | 409 | 31.8 | 367 | 7.8 | 88 | 447 | 77.5 |  |  |  | 89.7196 | 76.9892
|  | 1:30:pm | 14 | 4 | 360 | 7.5 | 2.2 | 391 | 6 | 365 | 7.6 | 21.4 | 400 | 27.4 | 370 | 7.8 | 93 | 441 | 71.6 |  |  |  | 85 | 76.9892
Thursday | 2010-01-14 | 9:30:am | 14 | 4 | 345 | 7.4 | 4.5 | 365 | 12 | 349 | 7.6 | 30 | 372 | 23.8 | 372 | 7.8 | 47 | 387 | 65 | 1200 | 44 | 11000 | 85.1852 | 50.9091
|  | 11:30:am | 15 | 4 | 349 | 7.5 | 4 | 369 | 11 | 353 | 7.7 | 27 | 377 | 20.6 | 377 | 7.8 | 55 | 396 | 54 |  |  |  | 82.2727 | 62.7119
|  | 1:30:pm | 16 | 4 | 353 | 7.5 | 3.9 | 373 | 9 | 357 | 7.7 | 22 | 382 | 18.5 | 382 | 7.8 | 59 | 399 | 48 |  |  |  | 89.1304 | 54.902
Friday | 2010-01-15 | 9:30:am | 15 | 4.5 | 344 | 7.4 | 2.5 | 364 | 11 | 348 | 7.5 | 23 | 367 | 23 | 355 | 7.6 | 51 | 374 | 44 | 1200 | 47 | 11000 | 88.5 | 63.6364
|  | 11:30:am | 16 | 4.3 | 348 | 7.5 | 2.3 | 361 | 9 | 353 | 7.6 | 20 | 364 | 21 | 361 | 7.7 | 55 | 377 | 41 |  |  |  | 88.2353 | 65.3061
|  | 1:30:pm | 17 | 4 | 351 | 7.5 | 2 | 355 | 7 | 357 | 7.6 | 17 | 360 | 18 | 366 | 7.8 | 49 | 381 | 37 |  |  |  | 89.5238 | 60.3774
Saturday | 2010-01-16 | 9:30:am | 14 | 4.8 | 341 | 7.5 | 2.2 | 373 | 10 | 345 | 7.6 | 21 | 377 | 22 | 353 | 7.7 | 53 | 382 | 39 | 1200 | 45 | 11000 | 88.2353 | 64.5833
|  | 11:30:am | 15 | 4.5 | 344 | 7.5 | 2 | 368 | 8 | 350 | 7.6 | 17 | 372 | 19 | 359 | 7.7 | 48 | 385 | 33 |  |  |  | 87.8571 | 78.4615
|  | 1:30:pm | 16 | 4.2 | 349 | 7.6 | 1.7 | 362 | 6 | 353 | 7.7 | 14 | 366 | 16 | 366 | 7.8 | 65 | 381 | 30 |  |  |  | 92.8571 | 78.4615
Sunday | 2010-01-17 | 9:30:am | 14 | 4.6 | 352 | 7.6 | 2 | 366 | 10.8 | 356 | 7.7 | 28 | 633 | 39.2 | 361 | 7.8 | 43 | 333 | 40 | 1050 | 47 | 11000 | 92.2727 | 51.1111
|  | 11:30:am | 15 | 4.3 | 355 | 7.6 | 1.7 | 361 | 9.4 | 359 | 7.7 | 22 | 559 | 35.6 | 366 | 7.8 | 45 | 345 | 34 |  |  |  | 92.5 | 51.2195
|  | 1:30:pm | 17 | 4 | 359 | 7.6 | 1.5 | 355 | 8.8 | 364 | 7.7 | 20 | 534 | 31.2 | 372 | 7.8 | 41 | 348 | 29 |  |  |  | 86.9436 | 42.8814
Monday | 2010-01-18 | 9:30:am | 15 | 5 | 345 | 7.4 | 4.4 | 255 | 11 | 348 | 7.5 | 33.7 | 234 | 37.8 | 355 | 7.6 | 59 | 266 | 65 | 1250 | 49 | 11000 | 89.3899 | 39.1935
|  | 11:30:am | 16 | 4.7 | 348 | 7.5 | 4 | 259 | 9 | 352 | 7.6 | 37.7 | 244 | 41.9 | 359 | 7.7 | 62 | 274 | 69 |  |  |  | 79.1667 | 77.8947
|  | 1:30:pm | 17 | 4.3 | 350 | 7.6 | 3.5 | 263 | 7 | 355 | 7.6 | 16.8 | 252 | 36.7 | 363 | 7.7 | 76 | 277 | 71 |  |  |  | 85.1852 | 59.8649
Tuesday | 2010-01-19 | 9:30:am | 14 | 5 | 342 | 7.3 | 4.4 | 200 | 7.2 | 345 | 7.4 | 29.7 | 166 | 42.2 | 351 | 7.5 | 74 | 266 | 90 | 1500 | 47 | 11000 | 82.8194 | 72.6506
|  | 11:30:am | 15 | 4.5 | 346 | 7.4 | 3.9 | 211 | 6.3 | 347 | 7.5 | 22.7 | 174 | 39.6 | 357 | 7.6 | 83 | 271 | 83 |  |  |  | 79.7468 | 82.0455
|  | 1:30:pm | 16 | 4 | 351 | 7.5 | 3.2 | 219 | 8.7 | 353 | 7.6 | 15.8 | 188 | 33.7 | 364 | 7.7 | 88 | 279 | 77 |  |  |  | 87.7778 | 82.0455
Wednesday | 2010-01-20 | 9:30:am | 14 | 5 | 354 | 7.4 | 2.2 | 133 | 15.6 | 357 | 7.5 | 18 | 166 | 95.2 | 361 | 7.7 | 71 | 233 | 70 | 1350 | 48 | 11000 | 80.5882 | 74.6479
|  | 11:30:am | 15 | 4.7 | 358 | 7.5 | 3.3 | 143 | 12.4 | 362 | 7.6 | 17 | 174 | 82.3 | 368 | 7.8 | 77 | 241 | 73 |  |  |  | 95.2381 | 77.9221
|  | 1:30:pm | 17 | 4.2 | 361 | 7.6 | 3 | 155 | 10.4 | 368 | 7.7 | 63 | 179 | 74.1 | 372 | 7.7 | 83 | 248 | 77 |  |  |  | 87.0175 | 24.0964
Thursday | 2010-01-21 | 9:30:am | 15 | 4.4 | 345 | 7.5 | 3.7 | 233 | 8.6 | 349 | 7.6 | 28.5 | 239 | 23 | 353 | 7.7 | 67 | 377 | 45 | 1200 | 46 | 11000 | 87.4016 | 57.4627
|  | 11:30:am | 16 | 4.2 | 349 | 7.5 | 3.2 | 243 | 9.5 | 355 | 7.6 | 25.4 | 246 | 21 | 359 | 7.8 | 74 | 383 | 40 |  |  |  | 88.1356 | 65.6757
|  | 1:30:pm | 17 | 4 | 354 | 7.6 | 2.8 | 248 | 7.3 | 359 | 7.7 | 23.6 | 253 | 18 | 366 | 7.8 | 70 | 389 | 35 |  |  |  | 89.6429 | 66.2857
Friday | 2010-01-22 | 9:30:am | 14 | 4.6 | 348 | 7.4 | 2.9 | 342 | 9.5 | 352 | 7.5 | 28 | 348 | 29 | 355 | 7.6 | 59 | 365 | 34 | 1050 | 47 | 11000 | 90 | 52.5424
|  | 11:30:am | 15 | 4.2 | 352 | 7.4 | 2.5 | 339 | 7.3 | 356 | 7.5 | 25 | 342 | 25 | 359 | 7.7 | 55 | 369 | 29 |  |  |  | 90 | 54.5455
|  | 1:30:pm | 16 | 4 | 355 | 7.5 | 2.2 | 335 | 6.9 | 359 | 7.6 | 22 | 339 | 22 | 362 | 7.8 | 51 | 372 | 25 |  |  |  | 88.2759 | 56.8627
Saturday | 2010-01-23 | 9:30:am | 14 | 4.5 | 347 | 7.3 | 3.4 | 345 | 7 | 349 | 7.4 | 29 | 349 | 28 | 355 | 7.5 | 43 | 359 | 34 | 900 | 45 | 11000 | 90.3226 | 32.5581
|  | 11:30:am | 15 | 4.2 | 351 | 7.4 | 3 | 353 | 8.5 | 343 | 7.5 | 31 | 352 | 24 | 359 | 7.6 | 81 | 363 | 31 |  |  |  | 83.125 | 61.7284
|  | 1:30:pm | 16 | 4 | 355 | 7.5 | 2.7 | 358 | 6.7 | 348 | 7.6 | 16 | 357 | 21 | 362 | 7.7 | 45 | 369 | 28 |  |  |  | 80.6167 | 64.4444
Sunday | 2010-01-24 | 9:30:am | 13 | 4.2 | 351 | 7.4 | 4.4 | 133 | 2.4 | 353 | 7.5 | 22.7 | 166 | 30.8 | 356 | 7.6 | 42.8 | 266 | 30.8 | 900 | 45 | 11000 | 85.9649 | 46.9626
|  | 11:30:am | 14 | 4 | 353 | 7.5 | 4 | 141 | 4 | 358 | 7.6 | 28.5 | 173 | 33.7 | 362 | 7.7 | 47.4 | 269 | 27.5 |  |  |  | 84.4262 | 54.3925
|  | 1:30:pm | 15 | 4 | 356 | 7.5 | 3.8 | 149 | 6.2 | 362 | 7.6 | 24.4 | 179 | 31.3 | 368 | 7.8 | 53.5 | 274 | 31.7 |  |  |  | 64.9123 | 81
Monday | 2010-01-25 | 9:30:am | 13 | 5 | 352 | 7.3 | 4 | 233 | 7 | 355 | 7.4 | 11.4 | 237 | 23 | 358 | 7.5 | 60 | 243 | 36.6 | 750 | 48 | 11000 | 86.6197 | 81
|  | 11:30:am | 14 | 4.6 | 356 | 7.4 | 3.8 | 226 | 8.3 | 359 | 7.5 | 28.4 | 243 | 21.4 | 362 | 7.6 | 63 | 248 | 33.4 |  |  |  | 86.9048 | 61.2308
|  | 1:30:pm | 15 | 4.3 | 359 | 7.4 | 3.3 | 223 | 9.5 | 363 | 7.6 | 25.2 | 235 | 18.5 | 366 | 7.7 | 65 | 253 | 29.5 |  |  |  | 86.3333 | 52
Tuesday | 2010-01-26 | 9:30:am | 12 | 5 | 352 | 7.4 | 4.1 | 200 | 5.2 | 355 | 7.5 | 30 | 213 | 36.4 | 359 | 7.7 | 62.5 | 234 | 32.8 | 1050 | 44 | 11000 | 88.9881 | 51.7241
|  | 11:30:am | 13 | 4.5 | 357 | 7.5 | 3.7 | 206 | 7.8 | 359 | 7.6 | 33.6 | 245 | 31.7 | 366 | 7.8 | 69.6 | 242 | 34.7 |  |  |  | 88.8136 | 52.188
|  | 1:30:pm | 14 | 4.3 | 360 | 7.6 | 3.3 | 211 | 8.3 | 364 | 7.7 | 29.5 | 236 | 27.5 | 369 | 7.8 | 61.7 | 245 | 36.2 |  |  |  | 83.105 | 58.6792
Wednesday | 2010-01-27 | 9:30:am | 11 | 4.6 | 345 | 7.4 | 3.7 | 338 | 3.2 | 347 | 7.5 | 21.9 | 336 | 35.6 | 354 | 7.6 | 53 | 330 | 16 | _ | 47 | 11000 | 88 | 58.6792
|  | 11:30:am | 12 | 4.3 | 351 | 7.5 | 3.3 | 342 | 4.3 | 349 | 7.6 | 27.5 | 341 | 31.7 | 361 | 7.7 | 57 | 335 | 18 |  |  |  | 86.7257 | 51.7544
|  | 1:30:pm | 13 | 4 | 353 | 7.5 | 3 | 347 | 5.8 | 355 | 7.6 | 22.6 | 345 | 28.4 | 366 | 7.7 | 55 | 339 | 14 |  |  |  | 86.9565 | 58.9091
Thursday | 2010-01-28 | 9:30:am | 13 | 4.4 | 349 | 7.3 | 3.3 | 333 | 12 | 352 | 7.4 | 25.3 | 339 | 23.7 | 344 | 7.5 | 73 | 345 | 23 | 900 | 44 | 11000 | 76.378 | 65.3425
|  | 11:30:am | 14 | 4 | 351 | 7.4 | 3 | 341 | 11 | 355 | 7.5 | 12.7 | 342 | 21.7 | 348 | 7.6 | 39 | 351 | 20 |  |  |  | 83.9286 | 67.4359
|  | 1:30:pm | 15 | 4 | 354 | 7.5 | 2.7 | 346 | 10 | 358 | 7.6 | 16.8 | 346 | 18.6 | 353 | 7.7 | 35 | 355 | 24 |  |  |  | 81.5126 | 52
Friday | 2010-01-29 | 9:30:am | 14 | 4.8 | 443 | 7.4 | 4.4 | 345 | 9 | 446 | 7.5 | 23.8 | 349 | 25.8 | 449 | 7.6 | 74 | 355 | 34 | 900 | 48 | 11000 | 83.7398 | 67.8378
|  | 11:30:am | 15 | 4.4 | 449 | 7.5 | 4 | 349 | 8 | 449 | 7.6 | 24.6 | 352 | 23.7 | 453 | 7.7 | 61 | 359 | 30 |  |  |  | 82.7907 | 59.6721
|  | 1:30:pm | 16 | 4.2 | 453 | 7.6 | 3.7 | 355 | 7 | 455 | 7.7 | 21.5 | 358 | 20.5 | 459 | 7.8 | 38 | 363 | 25 |  |  |  | 84.3882 | 84.3882
Saturday | 2010-01-30 | 9:30:am | 15 | 4.6 | 441 | 7.5 | 3.7 | 354 | 12 | 445 | 7.6 | 23.7 | 356 | 27.5 | 449 | 7.7 | 49 | 359 | 33 | 1050 | 44 | 11000 | 84.5794 | 84.5794
|  | 11:30:am | 16 | 4.2 | 444 | 7.5 | 3.3 | 359 | 11 | 448 | 7.6 | 21.4 | 361 | 23.1 | 453 | 7.7 | 44 | 364 | 27 |  |  |  | 84.8958 | 84.8958
|  | 1:30:pm | 17 | 4 | 449 | 7.6 | 2.9 | 361 | 10 | 452 | 7.7 | 19.2 | 363 | 20.3 | 459 | 7.8 | 40 | 369 | 23 |  |  |  | 76.1905 | 76.1905
Sunday | 2010-01-31 | 9:30 | 11 | 4.7 | 345 | 7.4 | 5 | 336 | 11.6 | 348 | 7.5 | 21 | 330 | 22.7 | 352 | 7.6 | 31 | 320 | 22.8 | 900 | 45 | 11000 | 76.6667 | 76.6667
|  | 11:30 | 12 | 4.3 | 348 | 7.5 | 4.2 | 341 | 9.6 | 353 | 7.6 | 18 | 334 | 19.7 | 357 | 7.7 | 38 | 324 | 24.7 |  |  |  | 80.5263 | 80.5263
|  | 1:30:pm | 13 | 4 | 350 | 7.6 | 3.7 | 345 | 7.8 | 359 | 7.7 | 19 | 339 | 17.4 | 362 | 7.8 | 43 | 333 | 29.6 |  |  |  | 80.5263 | 80.5263

## 2
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-02-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr)
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | R-S | S-SUP
Monday | 2010-02-01 | \ | 13 | 5 | 342 | 7.3 | 4.7 | 332 | 6.8 | 345 | 7.4 | 28.2 | 328 | 48 | 349 | 7.5 | 56.5 | 326 | 35 | 600 | 48 | 11000 | 50.0885 | 83.3333
|  | 11:30:am | 14 | 4.6 | 345 | 7.4 | 4.2 | 339 | 5.7 | 349 | 7.5 | 34.8 | 332 | 41 | 355 | 7.6 | 69.7 | 333 | 38 |  |  |  | 50.0717 | 87.931
|  | 1:30:pm | 15 | 4.3 | 349 | 7.5 | 3.9 | 342 | 5 | 354 | 7.6 | 30.6 | 338 | 36 | 361 | 7.7 | 63.6 | 341 | 42 |  |  |  | 51.8868 | 87.2549
Tuesday | 2010-02-02 | 9:30:am | 13 | 4.4 | 344 | 7.4 | 4 | 328 | 10 | 347 | 7.5 | 34.1 | 320 | 43.6 | 349 | 7.6 | 73.1 | 322 | 41.2 | 750 | 45 | 11000 | 53.3516 | 88.2698
|  | 11:30:am | 14 | 4.2 | 347 | 7.5 | 3.7 | 333 | 8 | 349 | 7.6 | 30.6 | 324 | 34.8 | 355 | 7.7 | 76.7 | 326 | 35.4 |  |  |  | 60.1043 | 87.9085
|  | 1:30:pm | 15 | 4 | 350 | 7.5 | 3.3 | 338 | 7 | 353 | 7.6 | 26.4 | 328 | 29.7 | 359 | 7.7 | 78.5 | 329 | 30.8 |  |  |  | 66.3694 | 87.5
Wednesday | 2010-02-03 | 9:30:am | 14 | 4.1 | 344 | 7.4 | 2.8 | 328 | 8 | 348 | 7.5 | 32.7 | 322 | 28.6 | 352 | 7.6 | 70.8 | 318 | 23 | 600 | 44 | 11000 | 53.8136 | 91.4373
|  | 11:30:am | 15 | 4 | 348 | 7.4 | 2.4 | 333 | 7 | 351 | 7.5 | 29.5 | 326 | 26.3 | 355 | 7.6 | 78.6 | 324 | 20 |  |  |  | 62.4682 | 91.8644
|  | 1:30:pm | 16 | 4 | 351 | 7.5 | 2.2 | 339 | 6 | 355 | 7.6 | 24.3 | 330 | 23.6 | 359 | 7.7 | 71.6 | 329 | 19 |  |  |  | 66.0615 | 90.9465
Thursday | 2010-02-04 | 9:30:am | 12 | 4.5 | 344 | 7.3 | 4.2 | 349 | 13 | 349 | 7.4 | 31 | 355 | 25 | 355 | 7.5 | 119 | 369 | 48 | 2250 | 48 | 11000 | 73.9496 | 86.4516
|  | 11:30:am | 13 | 4.2 | 349 | 7.4 | 3.8 | 355 | 11 | 353 | 7.5 | 27 | 359 | 23 | 359 | 7.6 | 123 | 372 | 44 |  |  |  | 78.0488 | 85.9259
|  | 1:30:pm | 14 | 4 | 353 | 7.5 | 3.3 | 359 | 10 | 358 | 7.6 | 23 | 363 | 20 | 364 | 7.7 | 121 | 378 | 40 |  |  |  | 80.9917 | 85.6522
Friday | 2010-02-05 | 9:30:am | 13 | 4.8 | 341 | 7.4 | 3.9 | 363 | 12 | 345 | 7.5 | 35 | 366 | 29 | 349 | 7.6 | 133 | 366 | 53 | 2550 | 47 | 11000 | 73.6842 | 88.8571
|  | 11:30:am | 14 | 4.4 | 345 | 7.4 | 3.4 | 359 | 13 | 349 | 7.6 | 31 | 361 | 25 | 354 | 7.7 | 128 | 369 | 50 |  |  |  | 75.7812 | 89.0323
|  | 1:30:pm | 15 | 4.2 | 349 | 7.4 | 3 | 355 | 15 | 353 | 7.6 | 28 | 358 | 23 | 359 | 7.8 | 125 | 373 | 44 |  |  |  | 77.6 | 89.2857
Saturday | 2010-02-06 | 9:30:am | 11 | 5 | 348 | 7.4 | 3.3 | 366 | 11 | 352 | 7.6 | 33 | 369 | 27 | 356 | 7.7 | 126 | 369 | 41 | 2400 | 49 | 11000 | 73.8095 | 90
|  | 11:30:am | 12 | 4.6 | 351 | 7.5 | 3 | 359 | 12 | 357 | 7.7 | 27 | 363 | 23 | 362 | 7.7 | 123 | 374 | 38 |  |  |  | 78.0488 | 88.8889
|  | 1:30:pm | 13 | 4.3 | 355 | 7.5 | 2.9 | 369 | 13 | 361 | 7.7 | 23 | 373 | 20 | 369 | 7.8 | 120 | 381 | 33 |  |  |  | 80.8333 | 87.3913
Sunday | 2010-02-07 | 9:30:am | 10 | 5 | 344 | 7.3 | 3.1 | 326 | 2.4 | 348 | 7.4 | 29.2 | 322 | 26.4 | 353 | 7.5 | 116 | 322 | 59.6 | 2250 | 46 | 11000 | 74.8276 | 89.3836
|  | 11:30:am | 11 | 4.5 | 349 | 7.4 | 2.8 | 334 | 3.9 | 354 | 7.5 | 27.4 | 329 | 23.7 | 359 | 7.6 | 119 | 328 | 53.7 |  |  |  | 76.9748 | 89.781
|  | 1:30:pm | 12 | 4.2 | 353 | 7.5 | 2.6 | 343 | 4.2 | 358 | 7.6 | 23.6 | 335 | 20.5 | 363 | 7.7 | 123 | 331 | 49.6 |  |  |  | 80.813 | 88.9831
Monday | 2010-02-08 | 9:30:am | 10 | 5 | 344 | 7.3 | 3.8 | 330 | 3.2 | 348 | 7.4 | 20.6 | 326 | 12 | 352 | 7.5 | 76 | 328 | 55.6 | 1500 | 44 | 11000 | 72.8947 | 81.5534
|  | 11:30:am | 11 | 4.7 | 348 | 7.4 | 3.1 | 336 | 4.8 | 352 | 7.5 | 18.6 | 333 | 14 | 359 | 7.6 | 82 | 333 | 51.8 |  |  |  | 77.3171 | 83.3333
|  | 1:30:pm | 12 | 4.3 | 351 | 7.5 | 2.7 | 340 | 5.6 | 359 | 7.6 | 19.7 | 339 | 17 | 363 | 7.7 | 88 | 343 | 48.5 |  |  |  | 77.6136 | 86.2944
Tuesday | 2010-02-09 | 9:30:am | 11 | 5 | 346 | 7.3 | 2.7 | 334 | 3.6 | 349 | 7.4 | 18.6 | 328 | 23.6 | 352 | 7.5 | 150 | 322 | 131.6 | 2700 | 48 | 11000 | 87.6 | 85.4839
|  | 11:30:am | 12 | 4.7 | 349 | 7.4 | 2.3 | 339 | 4.9 | 354 | 7.5 | 22.6 | 333 | 20.5 | 358 | 7.6 | 165 | 329 | 100 |  |  |  | 86.303 | 89.823
|  | 1:30:pm | 13 | 4.4 | 352 | 7.5 | 2 | 342 | 5.3 | 359 | 7.6 | 20.7 | 338 | 17.9 | 363 | 7.7 | 171 | 333 | 91 |  |  |  | 87.8947 | 90.3382
Wednesday | 2010-02-10 | 9:30:am | 11 | 4.4 | 349 | 7.4 | 2.5 | 320 | 2 | 352 | 7.5 | 29.9 | 318 | 26.4 | 358 | 7.6 | 127 | 316 | 100.8 | 2700 | 48 | 11000 | 76.4567 | 91.6388
|  | 11:30:am | 12 | 4.2 | 352 | 7.5 | 2 | 324 | 3 | 359 | 7.6 | 26.4 | 325 | 23.6 | 364 | 7.7 | 133 | 322 | 95.6 |  |  |  | 80.1504 | 92.4242
|  | 1:30:pm | 14 | 4 | 355 | 7.6 | 2.2 | 329 | 5 | 362 | 7.7 | 22.4 | 329 | 18.7 | 369 | 7.8 | 139 | 325 | 88.5 |  |  |  | 83.8849 | 90.1786
Thursday | 2010-02-11 | 9:30:am | 12 | 5 | 344 | 7.3 | 2.3 | 320 | 7 | 348 | 7.4 | 19 | 318 | 22.7 | 349 | 7.5 | 130 | 318 | 45 | 2250 | 46 | 11000 | 85.3846 | 87.8947
|  | 11:30:am | 13 | 4.7 | 348 | 7.4 | 2.6 | 323 | 6 | 353 | 7.5 | 23 | 322 | 20.4 | 355 | 7.6 | 138 | 327 | 39 |  |  |  | 83.3333 | 88.6957
|  | 1:30:pm | 14 | 4.3 | 352 | 7.5 | 2 | 327 | 4 | 358 | 7.6 | 25 | 329 | 18.5 | 359 | 7.7 | 144 | 333 | 33 |  |  |  | 82.6389 | 92
Friday | 2010-02-12 | 9:30:am | 13 | 4.7 | 357 | 7.4 | 2.8 | 328 | 8 | 359 | 7.5 | 26 | 333 | 22 | 363 | 7.6 | 138 | 338 | 34 | 2700 | 49 | 11000 | 81.1594 | 89.2308
|  | 11:30:am | 14 | 4.3 | 361 | 7.5 | 2.6 | 333 | 9 | 361 | 7.6 | 23 | 337 | 20 | 368 | 7.7 | 145 | 342 | 39 |  |  |  | 84.1379 | 88.6957
|  | 1:30:pm | 16 | 4 | 365 | 7.6 | 2.3 | 338 | 7 | 363 | 7.7 | 20 | 341 | 19 | 371 | 7.8 | 151 | 347 | 44 |  |  |  | 86.755 | 88.5
Saturday | 2010-02-13 | 9:30:am | 13 | 4.6 | 353 | 7.5 | 3.3 | 333 | 7 | 355 | 7.6 | 29 | 338 | 24 | 359 | 7.7 | 146 | 342 | 54 | 2700 | 45 | 11000 | 80.137 | 88.6207
|  | 11:30:am | 15 | 4.2 | 359 | 7.6 | 3 | 336 | 8 | 362 | 7.7 | 27 | 342 | 21 | 362 | 7.7 | 152 | 348 | 59 |  |  |  | 82.2368 | 88.8889
|  | 1:30:pm | 17 | 4 | 366 | 7.6 | 2.7 | 341 | 6 | 369 | 7.7 | 22 | 345 | 17 | 368 | 7.8 | 158 | 352 | 65 |  |  |  | 86.0759 | 87.7273
Sunday | 2010-02-14 | 9:30:am | 14 | 4.7 | 343 | 7.4 | 2.7 | 320 | 7.2 | 347 | 7.5 | 26.4 | 320 | 26.8 | 351 | 7.6 | 140 | 322 | 140.4 | 2400 | 48 | 11000 | 81.1429 | 89.7727
|  | 11:30:am | 15 | 4.2 | 348 | 7.5 | 2.3 | 324 | 8.8 | 349 | 7.6 | 23.7 | 326 | 23.1 | 357 | 7.7 | 144 | 329 | 122.6 |  |  |  | 83.5417 | 90.2954
|  | 1:30:pm | 18 | 4 | 350 | 7.6 | 2 | 329 | 6.4 | 353 | 7.7 | 20.9 | 331 | 21.8 | 359 | 7.8 | 149 | 333 | 113.8 |  |  |  | 85.9732 | 90.4306
Monday | 2010-02-15 | 9:30:am | 15 | 5 | 349 | 7.4 | 3.3 | 324 | 1.2 | 352 | 7.5 | 19.3 | 324 | 25.6 | 355 | 7.6 | 105 | 332 | 111 | 1500 | 45 | 11000 | 81.619 | 82.9016
|  | 11:30:am | 17 | 4.4 | 354 | 7.5 | 3 | 329 | 2 | 357 | 7.6 | 16.7 | 330 | 22.9 | 361 | 7.7 | 114 | 339 | 100 |  |  |  | 85.3509 | 82.0359
|  | 1:30:pm | 19 | 4 | 359 | 7.6 | 2.8 | 333 | 1.7 | 363 | 7.7 | 18.9 | 335 | 20.8 | 369 | 7.8 | 123 | 343 | 91 |  |  |  | 84.6341 | 85.1852
Tuesday | 2010-02-16 | 9:30:am | 14 | 5 | 349 | 7.5 | 2.6 | 330 | 2 | 352 | 7.6 | 21.5 | 326 | 20.8 | 356 | 7.7 | 72 | 328 | 58 | 1050 | 47 | 11000 | 70.1389 | 87.907
|  | 11:30:am | 16 | 4.6 | 353 | 7.5 | 2.2 | 337 | 3 | 358 | 7.6 | 18.5 | 333 | 22.5 | 362 | 7.7 | 83 | 335 | 48 |  |  |  | 77.7108 | 88.1081
|  | 1:30:pm | 17 | 4.2 | 358 | 7.6 | 2 | 341 | 5 | 362 | 7.7 | 19.5 | 339 | 21.4 | 369 | 7.8 | 94 | 342 | 44 |  |  |  | 79.2553 | 89.7436
Wednesday | 2010-02-17 | 9:30:am | 15 | 4.5 | 349 | 7.4 | 2.6 | 330 | 2 | 352 | 7.5 | 19.7 | 336 | 22.4 | 358 | 7.6 | 79 | 334 | 66.8 | 1200 | 45 | 11000 | 75.0633 | 86.802
|  | 11:30:am | 17 | 4.2 | 355 | 7.5 | 2.2 | 335 | 4 | 358 | 7.6 | 17.4 | 339 | 20.7 | 364 | 7.7 | 85 | 339 | 61.7 |  |  |  | 79.5294 | 87.3563
|  | 1:30:pm | 19 | 4 | 359 | 7.6 | 2 | 339 | 5 | 362 | 7.7 | 18.3 | 343 | 18.8 | 369 | 7.8 | 88 | 343 | 55.3 |  |  |  | 79.2045 | 89.071
Thursday | 2010-02-18 | 9:30:am | 14 | 4.7 | 348 | 7.3 | 3.3 | 342 | 9.7 | 351 | 7.4 | 22.8 | 345 | 24.2 | 355 | 7.5 | 99 | 349 | 88.9 | 1200 | 49 | 11000 | 76.9697 | 85.5263
|  | 11:30:am | 15 | 4.3 | 353 | 7.4 | 3 | 347 | 8.6 | 355 | 7.5 | 20.4 | 348 | 22.6 | 361 | 7.6 | 109 | 356 | 73.8 |  |  |  | 81.2844 | 85.2941
|  | 1:30:pm | 16 | 4 | 356 | 7.5 | 2.7 | 349 | 7.4 | 359 | 7.6 | 18.3 | 352 | 20.9 | 366 | 7.7 | 111 | 359 | 68.4 |  |  |  | 83.5135 | 85.2459
Friday | 2010-02-19 | 9:30:am | 12 | 4.5 | 349 | 7.4 | 2.8 | 349 | 11.6 | 354 | 7.5 | 18.5 | 352 | 28.6 | 358 | 7.6 | 116 | 356 | 56.8 | 1500 | 47 | 11000 | 84.0517 | 84.8649
|  | 11:30:am | 13 | 4.2 | 355 | 7.5 | 2.5 | 352 | 9.8 | 358 | 7.6 | 16.4 | 357 | 24.2 | 363 | 7.7 | 111 | 359 | 51.7 |  |  |  | 85.2252 | 84.7561
|  | 1:30:pm | 14 | 4 | 358 | 7.5 | 2.2 | 355 | 8.6 | 362 | 7.6 | 16.9 | 360 | 21.8 | 366 | 7.8 | 102 | 365 | 55.8 |  |  |  | 83.4314 | 86.9822
Saturday | 2010-02-20 | 9:30:am | 14 | 4.8 | 353 | 7.5 | 2.6 | 349 | 12.5 | 358 | 7.6 | 25.3 | 353 | 29.7 | 364 | 7.7 | 123 | 358 | 94.8 | 2400 | 48 | 11000 | 79.4309 | 89.7233
|  | 11:30:am | 15 | 4.4 | 359 | 7.5 | 2.2 | 355 | 11.6 | 361 | 7.6 | 22.8 | 358 | 25.3 | 369 | 7.8 | 112 | 364 | 87.5 |  |  |  | 79.6429 | 90.3509
|  | 1:30:pm | 17 | 4.2 | 361 | 7.6 | 1.8 | 359 | 9.2 | 364 | 7.7 | 20.4 | 362 | 21.7 | 370 | 7.8 | 116 | 369 | 76.4 |  |  |  | 82.4138 | 91.1765
Sunday | 2010-02-21 | 9:30:am | 14 | 4.3 | 345 | 7.4 | 2.9 | 353 | 11.9 | 348 | 7.5 | 22.1 | 357 | 20.7 | 353 | 7.6 | 92 | 361 | 45.7 | 1200 | 49 | 11000 | 75.9783 | 86.8778
|  | 11:30:am | 16 | 4 | 348 | 7.5 | 3 | 358 | 10.3 | 352 | 7.6 | 18.9 | 362 | 18.5 | 356 | 7.7 | 99 | 368 | 49.3 |  |  |  | 80.9091 | 84.127
|  | 1:30:pm | 18 | 4 | 350 | 7.6 | 3.3 | 360 | 8.8 | 355 | 7.7 | 17.4 | 365 | 17.5 | 361 | 7.8 | 112 | 373 | 55.4 |  |  |  | 84.4643 | 81.0345
Monday | 2010-02-22 | 9:30:am | 15 | 4.7 | 348 | 7.3 | 3.9 | 361 | 7.8 | 352 | 7.4 | 23 | 364 | 19.6 | 358 | 7.5 | 155 | 369 | 100 | 2250 | 44 | 11000 | 85.1613 | 83.0435
|  | 11:30:am | 16 | 4.3 | 351 | 7.4 | 3.6 | 366 | 8.4 | 358 | 7.5 | 21 | 371 | 17.6 | 366 | 7.6 | 159 | 374 | 112 |  |  |  | 86.7925 | 82.8571
|  | 1:30:pm | 18 | 4 | 358 | 7.5 | 3 | 369 | 8.8 | 364 | 7.6 | 18 | 375 | 18.4 | 374 | 7.7 | 165 | 379 | 118 |  |  |  | 89.0909 | 83.3333
Tuesday | 2010-02-23 | 9:30:am | 14 | 5 | 349 | 7.4 | 5 | 364 | 5.4 | 355 | 7.5 | 71 | 376 | 64.4 | 362 | 7.6 | 206 | 378 | 203 | 3750 | 49 | 11000 | 65.534 | 92.9577
|  | 11:30:am | 15 | 4.6 | 352 | 7.5 | 4.7 | 369 | 7.9 | 359 | 7.6 | 66 | 384 | 59.7 | 369 | 7.7 | 231 | 385 | 178 |  |  |  | 71.4286 | 92.8788
|  | 1:30:pm | 17 | 4.2 | 357 | 7.6 | 4 | 374 | 9.8 | 363 | 7.7 | 59 | 388 | 55.2 | 374 | 7.8 | 239 | 389 | 166 |  |  |  | 75.3138 | 93.2203
Wednesday | 2010-02-24 | 9:30:am | 15 | 4.7 | 359 | 7.4 | 3.9 | 366 | 9.9 | 362 | 7.5 | 33 | 371 | 31 | 366 | 7.6 | 155 | 377 | 102 | 2250 | 48 | 11000 | 78.7097 | 88.1818
|  | 11:30:am | 16 | 4.2 | 364 | 7.4 | 3.3 | 369 | 11.5 | 366 | 7.5 | 27 | 374 | 27 | 371 | 7.7 | 149 | 383 | 95 |  |  |  | 81.8792 | 87.7778
|  | 1:30:pm | 18 | 4 | 368 | 7.5 | 3 | 373 | 10.6 | 373 | 7.6 | 22 | 377 | 24 | 379 | 7.8 | 141 | 389 | 88 |  |  |  | 84.3972 | 86.3636
Thursday | 2010-02-25 | 9:30:am | 16 | 5 | 355 | 7.5 | 2.9 | 355 | 11.7 | 358 | 7.6 | 17.6 | 358 | 21 | 363 | 7.7 | 100 | 366 | 69 | 1800 | 47 | 11000 | 82.4 | 83.5227
|  | 11:30:am | 17 | 4.5 | 358 | 7.6 | 2.3 | 361 | 9.5 | 362 | 7.7 | 15.3 | 363 | 19 | 367 | 7.8 | 109 | 372 | 73 |  |  |  | 85.9633 | 84.9673
|  | 1:30:pm | 19 | 4.3 | 360 | 7.6 | 2 | 359 | 8.4 | 365 | 7.7 | 16.9 | 366 | 17 | 370 | 7.8 | 114 | 375 | 77 |  |  |  | 85.1754 | 88.1657
Friday | 2010-02-26 | 9:30:am | 14 | 4.5 | 349 | 7.4 | 3.6 | 345 | 9.5 | 352 | 7.5 | 23.9 | 349 | 20 | 355 | 7.6 | 99 | 353 | 34 | 1800 | 46 | 11000 | 75.8586 | 84.9372
|  | 11:30:am | 15 | 4.2 | 353 | 7.5 | 3.2 | 349 | 10.6 | 355 | 7.6 | 25.6 | 355 | 18 | 359 | 7.7 | 93 | 358 | 30 |  |  |  | 72.4731 | 87.5
|  | 1:30:pm | 16 | 4 | 358 | 7.6 | 2.8 | 353 | 8.4 | 361 | 7.7 | 22.8 | 358 | 16 | 364 | 7.8 | 86 | 363 | 28 |  |  |  | 73.4884 | 87.7193
Saturday | 2010-02-27 | 9:30:am | 12 | 4.8 | 352 | 7.3 | 2.9 | 349 | 11.3 | 354 | 7.4 | 26.9 | 352 | 22 | 357 | 7.5 | 82 | 356 | 39 | 1200 | 48 | 11000 | 67.1951 | 89.2193
|  | 11:30:am | 13 | 4.4 | 355 | 7.4 | 2.4 | 348 | 12.6 | 357 | 7.5 | 23.5 | 354 | 19 | 360 | 7.6 | 77 | 359 | 36 |  |  |  | 69.4805 | 89.7872
|  | 1:30:pm | 14 | 4.2 | 359 | 7.5 | 2.2 | 351 | 9.7 | 360 | 7.6 | 21.7 | 358 | 16 | 366 | 7.7 | 71 | 363 | 33 |  |  |  | 69.4366 | 89.8618
Sunday | 2010-02-28 | 9:30:am | 13 | 4.9 | 347 | 7.4 | 2.6 | 348 | 11.6 | 349 | 7.5 | 15.6 | 340 | 21.6 | 354 | 7.6 | 54 | 340 | 42.8 | 900 | 49 | 11000 | 71.1111 | 83.3333
|  | 11:30:am | 14 | 4.6 | 349 | 7.5 | 2.4 | 352 | 9.8 | 352 | 7.6 | 18.5 | 344 | 17.5 | 359 | 7.7 | 60 | 348 | 37.4 |  |  |  | 69.1667 | 87.027
|  | 1:30:pm | 15 | 4.3 | 353 | 7.6 | 2.2 | 355 | 8.7 | 355 | 7.7 | 17.5 | 349 | 15.3 | 362 | 7.8 | 63 | 353 | 29.9 |  |  |  | 72.2222 | 87.4286

## 3
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-03-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr) | S-R | S-SUP
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS
Monday | 2010-03-01 | 9:30:am | 13 | 5 | 359 | 7.3 | 5 | 346 | 6.8 | 363 | 7.4 | 72 | 334 | 70 | 369 | 7.5 | 258 | 280 | 308 | 4500 | 48 | 11000 | 72.093 | 93.0556
|  | 11:30:am | 14 | 4.6 | 366 | 7.4 | 4.3 | 351 | 8.2 | 368 | 7.5 | 69 | 344 | 66 | 374 | 7.6 | 263 | 295 | 296 |  |  |  | 73.7643 | 93.7681
|  | 1:30:pm | 15 | 4.2 | 369 | 7.5 | 4 | 356 | 9.7 | 374 | 7.6 | 66 | 352 | 58 | 379 | 7.7 | 277 | 312 | 291 |  |  |  | 76.1733 | 93.9394
Tuesday | 2010-03-02 | 9:30:am | 14 | 5 | 366 | 7.4 | 3.4 | 336 | 16 | 371 | 7.5 | 68 | 334 | 61.6 | 377 | 7.6 | 401 | 332 | 370 | 5250 | 49 | 11000 | 83.0424 | 95
|  | 11:30:am | 16 | 4.7 | 369 | 7.5 | 3 | 343 | 13 | 375 | 7.6 | 63 | 341 | 55.3 | 383 | 7.7 | 423 | 339 | 345 |  |  |  | 85.1064 | 95.2381
|  | 1:30:pm | 18 | 4.5 | 373 | 7.6 | 2.8 | 349 | 11 | 379 | 7.7 | 58 | 347 | 44.3 | 389 | 7.8 | 436 | 347 | 322 |  |  |  | 86.6972 | 95.1724
Wednesday | 2010-03-03 | 9:30:am | 13 | 5 | 366 | 7.4 | 4.8 | 300 | 14 | 369 | 7.5 | 49.7 | 290 | 39.6 | 373 | 7.6 | 244 | 268 | 219.2 | 3000 | 48 | 11000 | 79.6311 | 90.3421
|  | 11:30:am | 15 | 4.7 | 373 | 7.5 | 4.5 | 321 | 11 | 375 | 7.6 | 41.6 | 281 | 32.5 | 379 | 7.7 | 258 | 276 | 193.5 |  |  |  | 83.876 | 89.1827
|  | 1:30:pm | 17 | 4.3 | 379 | 7.6 | 4.2 | 333 | 9 | 379 | 7.7 | 36.2 | 276 | 28.6 | 382 | 7.8 | 266 | 284 | 188.4 |  |  |  | 86.391 | 88.3978
Thursday | 2010-03-04 | 9:30:am | 15 | 4.6 | 371 | 7.3 | 3.9 | 345 | 13 | 373 | 7.4 | 33.6 | 341 | 28 | 376 | 7.5 | 185 | 338 | 100 | 2100 | 47 | 11000 | 81.8378 | 88.3929
|  | 11:30:am | 17 | 4.2 | 375 | 7.4 | 3.5 | 349 | 11 | 378 | 7.5 | 30.5 | 346 | 25 | 381 | 7.6 | 178 | 343 | 90 |  |  |  | 82.8652 | 88.5246
|  | 1:30:pm | 19 | 4 | 381 | 7.5 | 3.2 | 352 | 10 | 382 | 7.6 | 27.4 | 350 | 22 | 385 | 7.7 | 171 | 348 | 81 |  |  |  | 83.9766 | 88.3212
Friday | 2010-03-05 | 9:30:am | 14 | 4.4 | 361 | 7.4 | 3 | 355 | 13 | 366 | 7.5 | 25.4 | 351 | 22 | 368 | 7.6 | 123 | 345 | 88 | 1800 | 45 | 11000 | 79.3496 | 88.189
|  | 11:30:am | 15 | 4.2 | 367 | 7.5 | 2.7 | 350 | 11 | 369 | 7.6 | 21.6 | 347 | 18 | 372 | 7.7 | 111 | 342 | 81 |  |  |  | 80.5405 | 87.5
|  | 1:30:pm | 16 | 4 | 370 | 7.5 | 2.3 | 346 | 8 | 373 | 7.7 | 18.5 | 344 | 16 | 377 | 7.8 | 106 | 340 | 72 |  |  |  | 82.5472 | 87.5676
Saturday | 2010-03-06 | 9:30:am | 16 | 4.7 | 345 | 7.4 | 2.9 | 353 | 14 | 349 | 7.5 | 24 | 356 | 21 | 352 | 7.6 | 97 | 360 | 65 | 1500 | 47 | 11000 | 75.2577 | 87.9167
|  | 11:30:am | 18 | 4.3 | 349 | 7.4 | 2.6 | 356 | 12 | 352 | 7.5 | 21 | 360 | 19 | 358 | 7.6 | 89 | 365 | 54 |  |  |  | 76.4045 | 87.619
|  | 1:30:pm | 19 | 4 | 352 | 7.5 | 2.3 | 359 | 10 | 355 | 7.6 | 18 | 362 | 16 | 362 | 7.7 | 84 | 369 | 48 |  |  |  | 78.5714 | 87.2222
Sunday | 2010-03-07 | 9:30:am | 16 | 4.6 | 351 | 7.3 | 3.4 | 345 | 11 | 356 | 7.4 | 25 | 342 | 27 | 359 | 7.5 | 112 | 341 | 44 | 1250 | 46 | 11000 | 77.6786 | 86.4
|  | 11:30:am | 18 | 4.3 | 355 | 7.4 | 3 | 348 | 9 | 360 | 7.5 | 22 | 346 | 24 | 363 | 7.6 | 106 | 345 | 41 |  |  |  | 79.2453 | 86.3636
|  | 1:30:pm | 20 | 4 | 358 | 7.5 | 2.7 | 351 | 7 | 363 | 7.6 | 20 | 349 | 20 | 368 | 7.7 | 102 | 349 | 38 |  |  |  | 80.3922 | 86.5
Monday | 2010-03-08 | 9:30:am | 15 | 4.8 | 348 | 7.5 | 3 | 349 | 12 | 352 | 7.6 | 28 | 347 | 23 | 357 | 7.7 | 100 | 345 | 34 | 1150 | 49 | 11000 | 72 | 89.2857
|  | 11:30:am | 17 | 4.5 | 352 | 7.5 | 2.6 | 353 | 11 | 357 | 7.6 | 24 | 351 | 21 | 359 | 7.7 | 94 | 349 | 31 |  |  |  | 74.4681 | 89.1667
|  | 1:30:pm | 18 | 4.2 | 355 | 7.4 | 2.2 | 358 | 9 | 360 | 7.5 | 22 | 356 | 18 | 363 | 7.6 | 88 | 353 | 29 |  |  |  | 75 | 90
Tuesday | 2010-03-09 | 9:30:am | 17 | 4.4 | 347 | 7.4 | 3.3 | 353 | 6 | 351 | 7.5 | 26 | 349 | 34 | 356 | 7.6 | 98 | 344 | 59 | 1150 | 46 | 11000 | 73.4694 | 87.3077
|  | 11:30:am | 19 | 4.2 | 351 | 7.5 | 3 | 359 | 7 | 356 | 7.6 | 23 | 354 | 29 | 362 | 7.7 | 93 | 351 | 55 |  |  |  | 75.2688 | 86.9565
|  | 1:30:pm | 22 | 4 | 355 | 7.6 | 2.6 | 363 | 9 | 359 | 7.7 | 20 | 360 | 27 | 367 | 7.8 | 90 | 357 | 51 |  |  |  | 77.7778 | 87
Wednesday | 2010-03-10 | 9:30:am | 17 | 4.6 | 349 | 7.5 | 2.4 | 384 | 6 | 353 | 7.6 | 44.2 | 378 | 54.8 | 358 | 7.7 | 110 | 370 | 104 | 1500 | 49 | 11000 | 59.8182 | 94.5701
|  | 11:30:am | 18 | 4.4 | 353 | 7.6 | 2 | 388 | 8 | 357 | 7.6 | 38.6 | 384 | 48.5 | 365 | 7.8 | 102 | 378 | 97 |  |  |  | 62.1569 | 94.8187
|  | 1:30:pm | 1`9 | 4.2 | 355 | 7.7 | 1.8 | 391 | 10 | 361 | 7.7 | 33.5 | 388 | 41.4 | 371 | 7.9 | 96 | 383 | 89 |  |  |  | 65.1042 | 94.6269
Thursday | 2010-03-11 | 9:30:am | 18 | 4.7 | 348 | 7.6 | 2 | 386 | 13 | 351 | 7.6 | 27.2 | 384 | 29 | 355 | 7.8 | 169 | 388 | 88 | 1500 | 47 | 11000 | 83.9053 | 92.6471
|  | 11:30:am | 20 | 4.3 | 351 | 7.6 | 1.7 | 378 | 11 | 355 | 7.7 | 22.6 | 379 | 25 | 361 | 7.9 | 145 | 380 | 74 |  |  |  | 84.4138 | 92.4779
|  | 1:30:pm | 22 | 4 | 353 | 7.7 | 1.5 | 372 | 9 | 358 | 7.7 | 21.5 | 368 | 22 | 365 | 7.9 | 138 | 377 | 71 |  |  |  | 84.4203 | 93.0233
Friday | 2010-03-12 | 9:30:am | PROJECT SHUT DOWN
11:30:am
1:30:pm
Saturday | 2010-03-13 | 9:30:am
11:30:am
1:30:pm
Sunday | 2010-03-14 | 9:30:am
11:30:am
1:30:pm
Monday | 2010-03-15 | 9:30:am
11:30:am
1:30:pm
Tuesday | 2010-03-16 | 9:30:am
11:30:am
1:30:pm
Wednesday | 2010-03-17 | 9:30:am | 20 | 5 | 363 | 7.4 | 5 | 386 | 27.6 | 369 | 7.9 | 100 | 406 | 148.6 | 373 | 8 | 253 | 434 | 264.3 | 1500 | 48 | 11000 | 60.4743 | 95
|  | 11:30:am | 22 | 4.5 | 367 | 7.5 | 4.7 | 396 | 21.7 | 376 | 7.8 | 129 | 421 | 123.7 | 377 | 7.9 | 269 | 445 | 229.6 |  |  |  | 52.0446 | 96.3566
|  | 1:30:pm | 25 | 4.2 | 371 | 7.6 | 4 | 404 | 19.6 | 383 | 7.8 | 100 | 431 | 110.7 | 379 | 7.8 | 275 | 451 | 221.8 |  |  |  | 63.6364 | 96
Thursday | 2010-03-18 | 9:30:am | 18 | 5 | 368 | 7.3 | 5 | 396 | 16 | 371 | 7.7 | 51 | 388 | 28 | 375 | 7.9 | 102 | 384 | 90 | 1500 | 47 | 11000 | 50 | 90.1961
|  | 11:30:am | 20 | 4.4 | 372 | 7.4 | 4.2 | 403 | 11 | 378 | 7.8 | 46 | 393 | 25 | 381 | 7.9 | 116 | 391 | 82 |  |  |  | 60.3448 | 90.8696
|  | 1:30:pm | 22 | 4.2 | 375 | 7.5 | 3.7 | 408 | 10 | 382 | 7.9 | 59 | 399 | 22 | 388 | 8 | 123 | 399 | 74 |  |  |  | 52.0325 | 93.7288
Friday | 2010-03-19 | 9:30:am | 23 | 4.4 | 366 | 7.4 | 4 | 388 | 13 | 369 | 7.6 | 44 | 383 | 25 | 373 | 7.8 | 111 | 380 | 75 | 1650 | 48 | 11000 | 60.3604 | 90.9091
|  | 11:30:am | 24 | 4.1 | 370 | 7.5 | 3.6 | 394 | 11 | 373 | 7.7 | 41 | 390 | 22 | 377 | 7.9 | 107 | 386 | 65 |  |  |  | 61.6822 | 91.2195
|  | 1:30:pm | 26 | 4 | 374 | 7.6 | 3 | 398 | 9 | 377 | 7.8 | 37 | 393 | 19 | 383 | 7.9 | 100 | 390 | 61 |  |  |  | 63 | 91.8919
Saturday | 2010-03-20 | 9:30:am | 17 | 4.8 | 358 | 7.3 | 3.9 | 393 | 9 | 361 | 7.5 | 38 | 388 | 29 | 365 | 7.6 | 121 | 385 | 88 | 1800 | 46 | 11000 | 68.595 | 89.7368
|  | 11:30:am | 19 | 4.4 | 363 | 7.4 | 3.3 | 399 | 7 | 366 | 7.6 | 35 | 395 | 25 | 369 | 7.7 | 115 | 391 | 81 |  |  |  | 69.5652 | 90.5714
|  | 1:30:pm | 21 | 4 | 365 | 7.5 | 2.9 | 405 | 6 | 369 | 7.7 | 29 | 399 | 23 | 373 | 7.8 | 110 | 396 | 76 |  |  |  | 73.6364 | 90
Sunday | 2010-03-21 | 9:30:am | 20 | 4.7 | 351 | 7.4 | 3.6 | 381 | 15 | 355 | 7.6 | 31 | 377 | 27 | 360 | 7.7 | 129 | 373 | 95 | 1800 | 49 | 11000 | 75.969 | 88.3871
|  | 11:30:am | 22 | 4.3 | 355 | 7.5 | 3 | 377 | 12 | 358 | 7.7 | 27 | 371 | 22 | 365 | 7.8 | 133 | 369 | 87 |  |  |  | 79.6992 | 88.8889
|  | 1:30:pm | 25 | 4 | 358 | 7.6 | 2.7 | 372 | 10 | 362 | 7.8 | 23 | 367 | 18 | 368 | 7.9 | 126 | 363 | 76 |  |  |  | 81.746 | 88.2609
Monday | 2010-03-22 | 9:30:am | 17 | 5 | 357 | 7.3 | 5 | 370 | 2.4 | 361 | 7.6 | 45.1 | 368 | 40.4 | 365 | 7.8 | 194 | 362 | 100 | 2400 | 49 | 11000 | 76.7526 | 88.9135
|  | 11:30:am | 19 | 4.5 | 361 | 7.4 | 4.3 | 377 | 5 | 366 | 7.7 | 38.5 | 374 | 35.4 | 371 | 7.9 | 182 | 370 | 109 |  |  |  | 78.8462 | 88.8312
|  | 1:30:pm | 21 | 4.2 | 365 | 7.5 | 3.8 | 381 | 7 | 369 | 7.8 | 34.3 | 378 | 33.8 | 375 | 8 | 175 | 374 | 116 |  |  |  | 80.4 | 88.9213
Tuesday | 2010-03-23 | 9:30:am | 17 | 5 | 355 | 7.3 | 5 | 340 | 18.8 | 358 | 7.7 | 26.5 | 356 | 38 | 362 | 7.9 | 100 | 360 | 88 | 1450 | 48 | 11000 | 73.5 | 81.1321
|  | 11:30:am | 19 | 4.7 | 359 | 7.4 | 4.2 | 344 | 14.5 | 361 | 7.8 | 22.8 | 359 | 31 | 368 | 8 | 112 | 365 | 75 |  |  |  | 79.6429 | 81.5789
|  | 1:30:pm | 20 | 4.3 | 362 | 7.5 | 3.7 | 348 | 12.6 | 365 | 7.8 | 18.6 | 362 | 27 | 373 | 8 | 106 | 369 | 66 |  |  |  | 82.4528 | 80.1075
Wednesday | 2010-03-24 | 9:30:am | 17 | 4.7 | 349 | 7.4 | 4.4 | 360 | 10 | 352 | 7.7 | 21.5 | 364 | 32 | 355 | 7.9 | 89 | 362 | 56 | 1450 | 49 | 11000 | 75.8427 | 79.5349
|  | 11:30:am | 19 | 4.3 | 353 | 7.5 | 3.8 | 366 | 11 | 356 | 7.8 | 19.8 | 369 | 27 | 359 | 8 | 95 | 366 | 48 |  |  |  | 79.1579 | 80.8081
|  | 1:30:pm | 22 | 4 | 356 | 7.6 | 3.3 | 369 | 8 | 359 | 7.8 | 17.8 | 374 | 23 | 364 | 8 | 99 | 373 | 44 |  |  |  | 82.0202 | 81.4607
Thursday | 2010-03-25 | 9:30:am | 17 | 4.8 | 344 | 7.3 | 4.4 | 342 | 13 | 348 | 7.7 | 51 | 346 | 26 | 353 | 7.9 | 80 | 340 | 55 | 1450 | 47 | 11000 | 36.25 | 91.3725
|  | 11:30:am | 18 | 4.5 | 349 | 7.4 | 4 | 346 | 11 | 352 | 7.8 | 41 | 349 | 22 | 359 | 8 | 88 | 344 | 43 |  |  |  | 53.4091 | 90.2439
|  | 1:30:pm | 20 | 4.2 | 351 | 7.5 | 3.8 | 349 | 9 | 355 | 7.9 | 33 | 355 | 20 | 364 | 8 | 95 | 349 | 38 |  |  |  | 65.2632 | 88.4848
Friday | 2010-03-26 | 9:30:am | 18 | 4.6 | 349 | 7.4 | 3.8 | 355 | 15 | 353 | 7.6 | 39 | 352 | 32 | 357 | 7.8 | 98 | 350 | 65 | 1450 | 49 | 11000 | 60.2041 | 90.2564
|  | 11:30:am | 21 | 4.2 | 352 | 7.5 | 3.3 | 360 | 12 | 357 | 7.7 | 33 | 357 | 27 | 361 | 7.9 | 103 | 355 | 53 |  |  |  | 67.9612 | 90
|  | 1:30:pm | 23 | 4.3 | 357 | 7.6 | 2.8 | 366 | 10 | 361 | 7.8 | 28 | 361 | 22 | 369 | 7.9 | 111 | 358 | 48 |  |  |  | 74.7748 | 90
Saturday | 2010-03-27 | 9:30:am | 17 | 4.8 | 358 | 7.6 | 3.2 | 364 | 11 | 361 | 7.8 | 31 | 360 | 28 | 366 | 7.9 | 123 | 358 | 45 | 11600 | 51 | 11000 | 74.7967 | 89.6774
|  | 11:30:am | 19 | 4.4 | 361 | 7.7 | 3.5 | 368 | 13 | 366 | 7.8 | 26 | 365 | 25 | 372 | 7.9 | 132 | 363 | 34 |  |  |  | 80.303 | 86.5385
|  | 1:30:pm | 22 | 4.2 | 366 | 7.7 | 3 | 370 | 14 | 370 | 7.9 | 22 | 368 | 22 | 378 | 8 | 129 | 366 | 27 |  |  |  | 82.9457 | 86.3636
Sunday | 2010-03-28 | 9:30:am | 14 | 5 | 352 | 7.6 | 5 | 340 | 8 | 357 | 7.8 | 47.4 | 336 | 51.6 | 361 | 8 | 78 | 334 | 91.2 | 1650 | 49 | 11000 | 39.2308 | 89.4515
|  | 11:30:am | 15 | 4.6 | 355 | 7.5 | 4.3 | 345 | 6 | 359 | 7.7 | 41.7 | 341 | 44.3 | 366 | 7.9 | 84 | 341 | 87.6 |  |  |  | 50.3571 | 89.6882
|  | 1:30:pm | 17 | 4.2 | 359 | 7.6 | 3.8 | 349 | 7 | 363 | 7.9 | 33.6 | 347 | 38.5 | 369 | 8 | 88 | 345 | 77.4 |  |  |  | 61.8182 | 88.6905
Monday | 2010-03-29 | 9:30:am | 16 | 4.4 | 349 | 7.4 | 4.6 | 330 | 11 | 353 | 7.7 | 78 | 324 | 39 | 358 | 8 | 190 | 324 | 66 | 1250 | 48 | 11000 | 58.9474 | 94.1026
|  | 11:30:am | 18 | 4.2 | 353 | 7.5 | 4 | 336 | 9 | 356 | 7.8 | 46 | 329 | 42 | 363 | 7.9 | 120 | 329 | 53 |  |  |  | 61.6667 | 91.3043
|  | 1:30:pm | 19 | 4 | 356 | 7.6 | 3.6 | 342 | 8 | 359 | 7.9 | 38 | 332 | 38 | 368 | 8 | 88 | 333 | 47 |  |  |  | 56.8182 | 90.5263
Tuesday | 2010-03-30 | 9:30:am | 17 | 4.8 | 354 | 7.3 | 4.2 | 320 | 15.2 | 358 | 7.5 | 71 | 312 | 58 | 362 | 7.7 | 334 | 328 | 348 | 3150 | 47 | 11000 | 78.7425 | 94.0845
|  | 11:30:am | 19 | 4.5 | 358 | 7.4 | 3.8 | 328 | 13.6 | 362 | 7.6 | 64 | 322 | 43 | 367 | 7.8 | 346 | 335 | 333 |  |  |  | 81.5029 | 94.0625
|  | 1:30:pm | 21 | 4.3 | 360 | 7.5 | 3.2 | 333 | 11.5 | 366 | 7.7 | 57 | 329 | 37 | 371 | 7.9 | 352 | 342 | 300 |  |  |  | 83.8068 | 94.386
Wednesday | 2010-03-31 | 9:30 | 17 | 4.5 | 351 | 7.3 | 5 | 348 | 6 | 355 | 7.5 | 51 | 360 | 21.2 | 359 | 7.7 | 251 | 396 | 116.8 | 3150 | 46 | 11000 | 79.6813 | 90.1961
|  | 11:30 | 19 | 4.2 | 355 | 7.4 | 4 | 355 | 8 | 360 | 7.6 | 44 | 363 | 18.6 | 366 | 7.8 | 275 | 404 | 100 |  |  |  | 84 | 90.9091
|  | 1:30:pm | 22 | 4 | 359 | 7.5 | 3.3 | 358 | 9 | 364 | 7.7 | 36 | 367 | 19.5 | 369 | 7.9 | 266 | 411 | 95.5 |  |  |  | 86.4662 | 90.8333

## 4
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-04-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr) | R-S | S-SUP
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS
Thursday | 2010-04-01 | 9:30:am | 17 | 5 | 361 | 7.3 | 4.2 | 388 | 13 | 366 | 7.6 | 35.2 | 406 | 23 | 369 | 7.8 | 113 | 410 | 45 | 2500 | 49 | 11000 | 68.8496 | 88.0682
|  | 11:30:am | 19 | 4.6 | 366 | 7.4 | 3.7 | 393 | 11 | 369 | 7.8 | 28.5 | 412 | 20 | 373 | 7.9 | 121 | 422 | 40 |  |  |  | 76.4463 | 87.0175
|  | 1:30:pm | 23 | 4.3 | 369 | 7.5 | 3 | 397 | 9 | 371 | 7.8 | 22.3 | 415 | 18 | 377 | 8 | 116 | 431 | 33 |  |  |  | 80.7759 | 86.5471
Friday | 2010-04-02 | 9:30:am | 19 | 5 | 355 | 7.4 | 3.9 | 398 | 16.8 | 359 | 7.8 | 44 | 396 | 55.2 | 363 | 8 | 90 | 394 | 102 | 2100 | 46 | 12500 | 51.1111 | 91.1364
|  | 11:30:am | 22 | 4.6 | 359 | 7.5 | 3.3 | 404 | 13.7 | 363 | 7.9 | 37 | 401 | 48.4 | 368 | 8 | 99 | 399 | 93 |  |  |  | 62.6263 | 91.0811
|  | 1:30:pm | 25 | 4.3 | 362 | 7.6 | 2.8 | 410 | 11.4 | 366 | 7.9 | 33 | 405 | 44.2 | 370 | 8 | 103 | 402 | 88 |  |  |  | 67.9612 | 91.5152
Saturday | 2010-04-03 | 9:30:am | 19 | 4.7 | 349 | 7.5 | 4.8 | 396 | 13.7 | 353 | 7.8 | 45.2 | 398 | 29 | 358 | 8.1 | 92 | 402 | 70 | 1800 | 48 | 12500 | 50.8696 | 89.3805
|  | 11:30:am | 23 | 4.3 | 352 | 7.6 | 4 | 400 | 11.5 | 356 | 7.8 | 40.8 | 404 | 25 | 366 | 8 | 84 | 409 | 65 |  |  |  | 51.4286 | 90.1961
|  | 1:30:pm | 26 | 4 | 358 | 7.7 | 3.5 | 405 | 9.8 | 360 | 7.9 | 38.6 | 409 | 22 | 370 | 8 | 88 | 413 | 56 |  |  |  | 56.1364 | 90.9326
Sunday | 2010-04-04 | 9:30:am | 20 | 4.5 | 355 | 7.4 | 3.9 | 402 | 14.4 | 359 | 7.8 | 45.7 | 400 | 34 | 364 | 8 | 94 | 394 | 55 | 1500 | 49 | 12500 | 51.383 | 91.4661
|  | 11:30:am | 24 | 4.2 | 360 | 7.5 | 4.2 | 405 | 12.3 | 363 | 7.9 | 47.8 | 403 | 27 | 369 | 8.1 | 99 | 399 | 47 |  |  |  | 51.7172 | 91.2134
|  | 1:30:pm | 27 | 4 | 362 | 7.6 | 3.5 | 410 | 10.7 | 366 | 7.9 | 42.4 | 408 | 22 | 373 | 8.1 | 103 | 407 | 38 |  |  |  | 58.835 | 91.7453
Monday | 2010-04-05 | 9:30:am | 16 | 5 | 361 | 7.3 | 3.5 | 388 | 11.4 | 366 | 7.9 | 35.2 | 406 | 23 | 370 | 8 | 103 | 402 | 88 | 2500 | 49 | 11000 | 65.8252 | 90.0568
|  | 11:30:am | 19 | 5 | 366 | 7.4 | 3.9 | 393 | 13.7 | 369 | 7.8 | 28.5 | 412 | 20 | 358 | 8.1 | 82 | 402 | 70 |  |  |  | 65.2439 | 86.3158
|  | 1:30:pm | 20 | 4.3 | 300 | 7.4 | 4.2 | 397 | 11.5 | 371 | 7.8 | 22.3 | 415 | 18 | 366 | 8 | 84 | 409 | 65 |  |  |  | 73.4524 | 81.1659
Tuesday | 2010-04-06 | 9:30:am | 19 | 5 | 355 | 7.4 | 3.9 | 398 | 16.8 | 359 | 7.8 | 44 | 396 | 55.2 | 363 | 8 | 90 | 394 | 102 | 2100 | 46 | 12500 | 51.1111 | 91.1364
|  | 11:30:am | 25 | 4.3 | 362 | 7.6 | 2.8 | 410 | 11.4 | 366 | 7.9 | 33 | 405 | 44.2 | 370 | 8 | 103 | 402 | 88 |  |  |  | 67.9612 | 91.5152
|  | 1:30:pm | 19 | 4.7 | 349 | 7.5 | 4.8 | 396 | 13.7 | 353 | 7.8 | 45.2 | 398 | 29 | 358 | 8.1 | 92 | 402 | 70 |  |  |  | 50.8696 | 89.3805
Wednesday | 2010-04-07 | 9:30:am | 19 | 4.7 | 349 | 7.5 | 4.8 | 396 | 13.7 | 353 | 7.8 | 45.2 | 398 | 29 | 358 | 8.1 | 92 | 402 | 70 | 1800 | 48 | 12500 | 50.8696 | 89.3805
|  | 11:30:am | 24 | 4.2 | 360 | 7.5 | 4.2 | 405 | 12.3 | 363 | 7.9 | 47.8 | 403 | 27 | 369 | 8.1 | 99 | 399 | 47 |  |  |  | 51.7172 | 91.2134
|  | 1:30:pm | 26 | 4 | 358 | 7.7 | 3.5 | 405 | 9.8 | 360 | 7.9 | 38.6 | 409 | 22 | 370 | 8 | 88 | 413 | 56 |  |  |  | 56.1364 | 90.9326
Thursday | 2010-04-08 | 9:30:am | 20 | 4.5 | 355 | 7.4 | 3.9 | 402 | 14.4 | 359 | 7.8 | 45.7 | 400 | 34 | 364 | 8 | 94 | 394 | 55 | 1500 | 49 | 12500 | 51.383 | 91.4661
|  | 11:30:am | 24 | 4.2 | 360 | 7.5 | 4.2 | 405 | 12.3 | 363 | 7.9 | 47.8 | 403 | 27 | 369 | 8.1 | 99 | 399 | 47 |  |  |  | 51.7172 | 91.2134
|  | 1:30:pm | 20 | 4.3 | 300 | 7.4 | 4.2 | 397 | 11.5 | 371 | 7.8 | 22.3 | 415 | 18 | 366 | 8 | 84 | 409 | 65 |  |  |  | 73.4524 | 81.1659
Friday | 2010-04-09 | 9:30:am | SHUT DOWN
11:30:am
1:30:pm
Saturday | 2010-04-10 | 9:30:am
11:30:am
1:30:pm
Sunday | 2010-04-11 | 9:30:am | 16 | 4.5 | 353 | 7.4 | 3.9 | 402 | 14.2 | 355 | 7.8 | 45.6 | 405 | 34 | 366 | 8.8 | 120 | 397 | 54 | 1500 | 49 | 12500 | 62 | 91.4474
|  | 11:30:am | 19 | 4.5 | 343 | 7.5 | 4.6 | 396 | 13.4 | 355 | 7.8 | 45.6 | 395 | 25 | 356 | 8.6 | 96 | 407 | 74 |  |  |  | 52.5 | 89.9123
|  | 1:30:pm | 18 | 4.7 | 343 | 7.6 | 4.8 | 395 | 13.2 | 354 | 7.8 | 45.5 | 394 | 24 | 358 | 8.6 | 92 | 403 | 74 |  |  |  | 50.5435 | 89.4505
Monday | 2010-04-12 | 9:30:am | 17 | 5 | 364 | 7.4 | 4.1 | 388 | 13 | 364 | 7.8 | 35.4 | 404 | 24 | 355 | 7.8 | 115 | 416 | 43 | 2500 | 49 | 11000 | 69.2174 | 88.4181
|  | 11:30:am | 19 | 4.5 | 365 | 7.4 | 3.1 | 393 | 11 | 369 | 7.8 | 28.5 | 414 | 20 | 373 | 7.6 | 121 | 423 | 43 |  |  |  | 76.4463 | 89.1228
|  | 1:30:pm | 23 | 4.3 | 363 | 7.4 | 3 | 397 | 18 | 374 | 7.7 | 22.3 | 415 | 14 | 374 | 8 | 115 | 433 | 32 |  |  |  | 80.6087 | 86.5471
Tuesday | 2010-04-13 | 9:30:am | 19 | 5 | 353 | 7.5 | 3.5 | 398 | 16.1 | 359 | 7.6 | 44 | 395 | 55.2 | 364 | 8 | 90 | 394 | 102 | 2100 | 46 | 12500 | 51.1111 | 92.0455
|  | 11:30:am | 22 | 4.6 | 352 | 7.4 | 3.5 | 404 | 13.7 | 364 | 7.9 | 37 | 401 | 48.4 | 368 | 8 | 95 | 399 | 93 |  |  |  | 61.0526 | 90.5405
|  | 1:30:pm | 25 | 4.4 | 364 | 7.5 | 2.4 | 410 | 11.4 | 363 | 7.5 | 33 | 405 | 43 | 370 | 8 | 103 | 402 | 82 |  |  |  | 67.9612 | 92.7273
Wednesday | 2010-04-14 | 9:30:am | 19 | 4.4 | 345 | 7.4 | 4.4 | 396 | 13.7 | 353 | 7.6 | 45.2 | 398 | 29 | 358 | 8.1 | 85 | 402 | 70 | 1800 | 48 | 12500 | 46.8235 | 90.2655
|  | 11:30:am | 23 | 4.4 | 356 | 7.5 | 4 | 400 | 11.5 | 353 | 7.6 | 40.8 | 405 | 23 | 366 | 8 | 85 | 409 | 62 |  |  |  | 52 | 90.1961
|  | 1:30:pm | 26 | 4 | 355 | 7.6 | 3.8 | 404 | 9.8 | 363 | 7.6 | 38.1 | 406 | 23 | 370 | 8 | 88 | 413 | 52 |  |  |  | 56.7045 | 90.0262
Thursday | 2010-04-15 | 9:30:am | 20 | 4.5 | 353 | 7.6 | 3.8 | 404 | 14.4 | 353 | 7.5 | 45.2 | 402 | 34 | 364 | 8 | 95 | 394 | 55 | 1500 | 49 | 12500 | 52.4211 | 91.5929
|  | 11:30:am | 24 | 4.2 | 362 | 7.6 | 4.8 | 407 | 12.3 | 363 | 7.9 | 47.9 | 403 | 27 | 369 | 8.1 | 97 | 399 | 41 |  |  |  | 50.6186 | 89.9791
|  | 1:30:pm | 27 | 5 | 361 | 7.5 | 3.7 | 417 | 10.7 | 363 | 7.9 | 42.9 | 403 | 22 | 373 | 8.1 | 103 | 407 | 35 |  |  |  | 58.3495 | 91.3753
Friday | 2010-04-16 | 9:30:am | 16 | 4 | 364 | 7.3 | 3.5 | 384 | 11.1 | 366 | 7.9 | 35.8 | 403 | 23 | 370 | 8 | 107 | 402 | 85 | 2500 | 49 | 11000 | 66.5421 | 90.2235
|  | 11:30:am | 19 | 5 | 365 | 7.4 | 3.4 | 393 | 13.2 | 367 | 7.8 | 28.7 | 412 | 20 | 358 | 8.1 | 82 | 402 | 70 |  |  |  | 65 | 88.1533
|  | 1:30:pm | 20 | 4.4 | 303 | 7.4 | 4.4 | 394 | 11.6 | 371 | 7.8 | 22.3 | 413 | 14 | 366 | 8 | 87 | 409 | 65 |  |  |  | 74.3678 | 80.2691
Saturday | 2010-04-17 | 9:30:am | 19 | 5 | 353 | 7.4 | 3.1 | 394 | 16.6 | 357 | 7.8 | 44 | 396 | 55.2 | 363 | 8 | 97 | 394 | 103 | 2100 | 46 | 12500 | 54.6392 | 92.9545
|  | 11:30:am | 25 | 4.4 | 362 | 7.6 | 2.1 | 411 | 11.5 | 367 | 7.9 | 37 | 404 | 44 | 370 | 8 | 107 | 402 | 83 |  |  |  | 65.4206 | 94.3243
|  | 1:30:pm | 19 | 4.7 | 344 | 7.5 | 4.2 | 394 | 13.4 | 353 | 7.8 | 47 | 398 | 29 | 358 | 8.5 | 100 | 402 | 73 |  |  |  | 53 | 91.0638
Sunday | 2010-04-18 | 9:30:am | 19 | 4.3 | 342 | 7.5 | 4.1 | 394 | 12 | 356 | 7.9 | 45.2 | 394 | 29 | 358 | 8.1 | 120 | 403 | 73 | 1800 | 48 | 12500 | 62.3333 | 90.9292
|  | 11:30:am | 24 | 4.4 | 362 | 7.5 | 4.1 | 405 | 12 | 363 | 7.9 | 46 | 403 | 25 | 364 | 8.5 | 99 | 393 | 47 |  |  |  | 53.5354 | 91.087
|  | 1:30:pm | 26 | 4 | 352 | 7.7 | 3.3 | 404 | 9.8 | 367 | 7.9 | 38 | 404 | 22 | 370 | 8 | 88 | 413 | 53 |  |  |  | 56.8182 | 91.3158
Monday | 2010-04-19 | 9:30:am | 20 | 4.4 | 352 | 7.4 | 3.3 | 401 | 14.1 | 357 | 7.8 | 45.7 | 400 | 34 | 364 | 8 | 97 | 394 | 55 | 1500 | 49 | 12500 | 52.8866 | 92.779
|  | 11:30:am | 24 | 4.2 | 363 | 7.5 | 4.4 | 403 | 12.3 | 363 | 7.7 | 45 | 404 | 29 | 365 | 8.4 | 99 | 393 | 42 |  |  |  | 54.5455 | 90.2222
|  | 1:30:pm | 27 | 4 | 363 | 7.6 | 3.7 | 411 | 10.7 | 368 | 7.9 | 42.4 | 408 | 29 | 373 | 8.4 | 107 | 403 | 32 |  |  |  | 60.3738 | 91.2736
Tuesday | 2010-04-20 | 9:30:am | 16 | 5 | 362 | 7.3 | 3.7 | 388 | 11.1 | 366 | 7.9 | 35 | 404 | 23 | 375 | 8 | 103 | 402 | 84 | 2500 | 49 | 11000 | 66.0194 | 89.4286
|  | 11:30:am | 19 | 4 | 364 | 7.4 | 3.7 | 393 | 13.6 | 366 | 7.8 | 25.5 | 412 | 28 | 358 | 8.5 | 87 | 403 | 74 |  |  |  | 70.6897 | 85.4902
|  | 1:30:pm | 20 | 4.5 | 304 | 7.4 | 4.8 | 397 | 11.6 | 375 | 7.7 | 22.4 | 414 | 19 | 365 | 8 | 84 | 403 | 64 |  |  |  | 73.3333 | 78.5714
Wednesday | 2010-04-21 | 9:30:am | 19 | 5 | 354 | 7.4 | 3.9 | 398 | 16.5 | 354 | 7.5 | 44 | 394 | 55 | 363 | 8 | 97 | 393 | 104 | 2100 | 46 | 12500 | 54.6392 | 91.1364
|  | 11:30:am | 25 | 4.2 | 365 | 7.6 | 2.8 | 410 | 11.4 | 364 | 7.9 | 35 | 404 | 44 | 373 | 8 | 103 | 403 | 84 |  |  |  | 66.0194 | 92
|  | 1:30:pm | 19 | 4.4 | 344 | 7.5 | 4.5 | 396 | 13.7 | 352 | 7.8 | 45.2 | 398 | 26 | 358 | 8.5 | 123 | 403 | 73 |  |  |  | 63.252 | 90.0442
Thursday | 2010-04-22 | 9:30:am | 20 | 4.8 | 349 | 7.3 | 4 | 412 | 15.7 | 352 | 7.5 | 32.8 | 408 | 23.8 | 355 | 7.8 | 145 | 402 | 38.9 | 750 | 48 | 12500 | 77.3793 | 87.8049
|  | 11:30:am | 22 | 4.4 | 353 | 7.4 | 3.7 | 405 | 12.7 | 356 | 7.6 | 28.6 | 402 | 21.6 | 360 | 7.9 | 149 | 395 | 33.2 |  |  |  | 80.8054 | 87.0629
|  | 1:30:pm | 24 | 4.2 | 355 | 7.5 | 3 | 400 | 10.5 | 359 | 7.7 | 25.6 | 396 | 18.5 | 366 | 8 | 62 | 390 | 28.6 |  |  |  | 58.7097 | 88.2812
Friday | 2010-04-23 | 9:30:am | 23 | 5 | 342 | 7.4 | 3 | 419 | 11.6 | 345 | 7.6 | 36.8 | 413 | 25.6 | 349 | 7.8 | 83 | 400 | 33.8 | 750 | 49 | 12000 | 55.6627 | 91.8478
|  | 11:30:am | 25 | 4.7 | 345 | 7.5 | 2.8 | 411 | 9.8 | 348 | 7.7 | 33.6 | 406 | 22.7 | 353 | 7.8 | 91 | 396 | 28.6 |  |  |  | 63.0769 | 91.6667
|  | 1:30:pm | 26 | 4.3 | 349 | 7.6 | 2.5 | 407 | 8.6 | 351 | 7.8 | 29.4 | 399 | 19.4 | 358 | 7.9 | 46 | 391 | 25.7 |  |  |  | 36.087 | 91.4966
Saturday | 2010-04-24 | 9:30:am | 21 | 4.9 | 353 | 7.5 | 4 | 398 | 12.6 | 356 | 7.7 | 28.5 | 394 | 26.5 | 360 | 7.9 | 79 | 390 | 29.5 | 600 | 50 | 13000 | 63.9241 | 85.9649
|  | 11:30:am | 22 | 4.5 | 355 | 7.5 | 3.3 | 393 | 10.9 | 359 | 7.8 | 25.7 | 388 | 22.9 | 366 | 7.9 | 72 | 383 | 25.4 |  |  |  | 64.3056 | 87.1595
|  | 1:30:pm | 23 | 4.3 | 358 | 7.6 | 2.7 | 390 | 8.8 | 362 | 7.9 | 22.7 | 382 | 19.4 | 370 | 8 | 45 | 376 | 21.7 |  |  |  | 49.5556 | 88.1057
Sunday | 2010-04-25 | 9:30:am | 21 | 5 | 344 | 7.3 | 5 | 426 | 14.8 | 349 | 7.4 | 24.1 | 424 | 33 | 355 | 8 | 35.9 | 416 | 55 | 600 | 48 | 13000 | 32.8691 | 79.2531
|  | 11:30:am | 23 | 4.7 | 348 | 7.4 | 4.4 | 410 | 11.2 | 351 | 7.5 | 26.4 | 427 | 29 | 359 | 7.9 | 39.7 | 411 | 41 |  |  |  | 33.5013 | 83.3333
|  | 1:30:pm | 25 | 4.3 | 351 | 7.5 | 3.8 | 397 | 9.6 | 355 | 7.6 | 29.9 | 430 | 26 | 362 | 7.8 | 71.6 | 404 | 37 |  |  |  | 58.2402 | 87.291
Monday | 2010-04-26 | 9:30:am | 21 | 4.8 | 347 | 7.3 | 4.2 | 430 | 12.4 | 350 | 7.4 | 34.5 | 420 | 39 | 353 | 8 | 76.9 | 411 | 33.8 | 600 | 47 | 13000 | 55.1365 | 87.8261
|  | 11:30:am | 24 | 4.6 | 352 | 7.4 | 3.9 | 415 | 10.6 | 355 | 7.5 | 31.8 | 414 | 31 | 358 | 7.8 | 79.6 | 404 | 29.6 |  |  |  | 60.0503 | 87.7358
|  | 1:30:pm | 27 | 4.2 | 355 | 7.6 | 3.5 | 405 | 8.4 | 358 | 7.7 | 28.6 | 402 | 27 | 363 | 7.9 | 63.3 | 400 | 22.4 |  |  |  | 54.8183 | 87.7622
Tuesday | 2010-04-27 | 9:30:am | 22 | 4.6 | 351 | 7.2 | 4.2 | 420 | 13.4 | 354 | 7.4 | 31.7 | 402 | 35 | 359 | 7.8 | 63.4 | 392 | 28.5 | 600 | 45 | 13000 | 50 | 86.7508
|  | 11:30:am | 25 | 4.2 | 353 | 7.3 | 4.1 | 408 | 11.6 | 359 | 7.5 | 28.6 | 399 | 28 | 363 | 7.9 | 66.8 | 387 | 23.7 |  |  |  | 57.1856 | 85.6643
|  | 1:30:pm | 27 | 4 | 357 | 7.4 | 3.8 | 400 | 8.4 | 362 | 7.7 | 23.7 | 395 | 22 | 368 | 7.9 | 69.3 | 383 | 20.7 |  |  |  | 65.8009 | 83.9662
Wednesday | 2010-04-28 | 9:30:am | 22 | 4.4 | 353 | 7.2 | 4 | 390 | 15.7 | 356 | 7.4 | 40.9 | 408 | 28 | 360 | 7.7 | 82.2 | 402 | 39.5 | 750 | 49 | 13000 | 50.2433 | 90.22
|  | 11:30:am | 24 | 4.2 | 356 | 7.3 | 3.7 | 395 | 12.8 | 359 | 7.5 | 36.3 | 395 | 23 | 366 | 7.8 | 88.6 | 393 | 33.2 |  |  |  | 59.0293 | 89.8072
|  | 1:30:pm | 26 | 4 | 359 | 7.4 | 3.2 | 399 | 10.9 | 363 | 7.6 | 30.7 | 391 | 20 | 369 | 7.9 | 89.4 | 384 | 27.5 |  |  |  | 65.66 | 89.5765
Thursday | 2010-04-29 | 9:30:am | 22 | 4.8 | 351 | 7.4 | 4.8 | 420 | 13.7 | 354 | 7.8 | 43.2 | 420 | 25.6 | 359 | 7.9 | 90.4 | 416 | 28.7 | 750 | 48 | 13000 | 52.2124 | 88.8889
|  | 11:30:am | 24 | 4.4 | 355 | 7.5 | 4 | 425 | 11.5 | 359 | 7.8 | 37.5 | 399 | 22.2 | 363 | 7.9 | 95 | 410 | 23.6 |  |  |  | 60.5263 | 89.3333
|  | 1:30:pm | 25 | 4 | 357 | 7.6 | 3.5 | 428 | 9.7 | 361 | 7.8 | 29.6 | 391 | 19.6 | 369 | 7.9 | 98 | 400 | 21.8 |  |  |  | 69.7959 | 88.1757
Friday | 2010-04-30 | 9:30:am | 20 | 4.6 | 350 | 7.3 | 3.9 | 399 | 8 | 352 | 7.5 | 27.5 | 395 | 22 | 355 | 7.7 | 95 | 391 | 27 | 750 | 49 | 13000 | 71.0526 | 85.8182
|  | 11:30:am | 21 | 4.2 | 351 | 7.4 | 3.3 | 410 | 9 | 355 | 7.6 | 23.3 | 405 | 20 | 359 | 7.8 | 93 | 397 | 24 |  |  |  | 74.9462 | 85.8369
|  | 1:30:pm | 22 | 4 | 353 | 7.5 | 2.8 | 413 | 11 | 357 | 7.7 | 21.9 | 409 | 18 | 364 | 7.9 | 98 | 400 | 21 |  |  |  | 77.6531 | 87.2146

## 5
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-05-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr)
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | S-R | S-SUP
Saturday | 2010-05-01 | 9:30:am | 22 | 4.5 | 351 | 7.4 | 3.9 | 412 | 12 | 355 | 7.6 | 27.9 | 405 | 25.8 | 358 | 7.8 | 64 | 400 | 34 | 900 | 47 | 12500 | 56.4062 | 86.0215
|  | 11:30:am | 23 | 4.2 | 356 | 7.5 | 3.3 | 399 | 10 | 358 | 7.7 | 23.6 | 392 | 21.6 | 362 | 7.9 | 67 | 390 | 27 |  |  |  | 64.7761 | 86.0169
|  | 1:30:pm | 25 | 4 | 358 | 7.6 | 2.8 | 395 | 8 | 363 | 7.8 | 21.3 | 387 | 17.3 | 366 | 8 | 61 | 382 | 25 |  |  |  | 65.082 | 86.8545
Saturday | 2010-05-02 | 9:30:am | 21 | 5 | 355 | 7.3 | 4.7 | 368 | 14 | 359 | 7.6 | 38.6 | 366 | 28.9 | 362 | 7.8 | 64 | 360 | 38 | 900 | 49 | 13000 | 39.6875 | 87.8238
|  | 11:30:am | 22 | 4.3 | 357 | 7.4 | 4 | 371 | 11 | 362 | 7.6 | 32.9 | 369 | 25.3 | 368 | 7.9 | 69 | 365 | 33 |  |  |  | 52.3188 | 87.8419
|  | 1:30:pm | 23 | 4 | 361 | 7.5 | 3.7 | 373 | 8 | 366 | 7.7 | 27.5 | 371 | 22.8 | 371 | 8 | 55 | 367 | 30 |  |  |  | 50 | 86.5455
Sunday | 2010-05-03 | 9:30:am | 21 | 5 | 347 | 7.3 | 3.4 | 380 | 12 | 350 | 7.7 | 36.3 | 378 | 25.9 | 355 | 7.9 | 73.8 | 378 | 34 | 1050 | 48 | 12000 | 50.813 | 90.6336
|  | 11:30:am | 22 | 4.6 | 349 | 7.4 | 3 | 386 | 10 | 354 | 7.8 | 33.4 | 383 | 22.9 | 359 | 8 | 77.7 | 380 | 31 |  |  |  | 57.0142 | 91.018
|  | 1:30:pm | 24 | 4.3 | 352 | 7.5 | 2.6 | 392 | 8 | 359 | 7.8 | 29.6 | 388 | 19.4 | 364 | 8 | 71.9 | 385 | 27 |  |  |  | 58.8317 | 91.2162
Monday | 2010-05-04 | 9:30:am | 22 | 4.7 | 344 | 7.2 | 4.6 | 370 | 10.4 | 349 | 7.6 | 40.3 | 370 | 42.6 | 354 | 7.9 | 84.7 | 368 | 40 | 900 | 49 | 13000 | 52.4203 | 88.5856
|  | 11:30:am | 24 | 4.3 | 347 | 7.4 | 4 | 374 | 8.6 | 353 | 7.7 | 33.7 | 373 | 36.4 | 357 | 7.9 | 87.9 | 371 | 35 |  |  |  | 61.661 | 88.1306
|  | 1:30:pm | 25 | 4 | 350 | 7.5 | 3.3 | 380 | 7.2 | 358 | 7.8 | 27.4 | 377 | 29.5 | 361 | 8 | 81.9 | 375 | 30 |  |  |  | 66.5446 | 87.9562
Tuesday | 2010-05-05 | 9:30:am | 22 | 4.8 | 348 | 7.2 | 3 | 360 | 18.4 | 351 | 7.6 | 57 | 368 | 72 | 358 | 7.8 | 100 | 406 | 71 | 1500 | 47 | 13000 | 43 | 94.7368
|  | 11:30:am | 24 | 4.4 | 352 | 7.3 | 2.7 | 369 | 14.3 | 354 | 7.7 | 49 | 367 | 66 | 364 | 7.9 | 110 | 392 | 68 |  |  |  | 55.4545 | 94.4898
|  | 1:30:pm | 26 | 4.2 | 355 | 7.4 | 2.5 | 372 | 11.5 | 358 | 7.8 | 41 | 369 | 52 | 369 | 8 | 88 | 388 | 66 |  |  |  | 53.4091 | 93.9024
Wednesday | 2010-05-06 | 9:30:am | 22 | 5 | 348 | 7.2 | 4.5 | 396 | 13.4 | 352 | 7.5 | 79 | 390 | 39 | 356 | 7.8 | 117 | 382 | 45 | 2400 | 48 | 13000 | 32.4786 | 94.3038
|  | 11:30:am | 24 | 4.6 | 355 | 7.3 | 3.8 | 400 | 11.6 | 359 | 7.6 | 66 | 395 | 31 | 362 | 7.9 | 140 | 388 | 40 |  |  |  | 52.8571 | 94.2424
|  | 1:30:pm | 25 | 4.2 | 357 | 7.4 | 3.3 | 410 | 9.7 | 362 | 7.7 | 55 | 405 | 27 | 368 | 7.9 | 133 | 395 | 38 |  |  |  | 58.6466 | 94
Thursday | 2010-05-07 | 9:30:am | 23 | 4.6 | 346 | 7.3 | 4.2 | 377 | 13.8 | 349 | 7.5 | 34.8 | 373 | 25.8 | 353 | 7.8 | 115 | 368 | 49.6 | 2400 | 47 | 12500 | 69.7391 | 87.931
|  | 11:30:am | 24 | 4.2 | 349 | 7.4 | 3.8 | 381 | 11.9 | 353 | 7.6 | 31.7 | 378 | 22.7 | 358 | 7.8 | 105 | 373 | 41.7 |  |  |  | 69.8095 | 88.0126
|  | 1:30:pm | 26 | 4 | 353 | 7.5 | 3.2 | 389 | 9.7 | 358 | 7.7 | 29.6 | 383 | 19.5 | 362 | 7.9 | 96 | 380 | 33.8 |  |  |  | 69.1667 | 89.1892
Friday | 2010-05-08 | 9:30:am | 22 | 4.8 | 348 | 7.4 | 3.9 | 364 | 15.4 | 351 | 7.6 | 43.8 | 361 | 34.8 | 355 | 7.8 | 100 | 358 | 59 | 2400 | 48 | 12500 | 56.2 | 91.0959
|  | 11:30:am | 24 | 4.5 | 352 | 7.5 | 3.3 | 368 | 13.8 | 356 | 7.7 | 35.8 | 363 | 30.5 | 359 | 7.9 | 91 | 361 | 47 |  |  |  | 60.6593 | 90.7821
|  | 1:30:pm | 27 | 4.2 | 357 | 7.6 | 2.6 | 370 | 11.4 | 359 | 7.8 | 28.6 | 368 | 28.5 | 365 | 7.9 | 84 | 366 | 40 |  |  |  | 65.9524 | 90.9091
Saturday | 2010-05-09 | 9:30:am | 24 | 4.7 | 353 | 7.3 | 2.9 | 359 | 14.9 | 356 | 7.6 | 33.9 | 357 | 45.7 | 361 | 7.7 | 119 | 353 | 55 | 2550 | 49 | 13000 | 71.5126 | 91.4454
|  | 11:30:am | 26 | 4.4 | 356 | 7.5 | 3.3 | 363 | 12.6 | 359 | 7.7 | 36.9 | 362 | 39.6 | 370 | 7.8 | 110 | 361 | 43 |  |  |  | 66.4545 | 91.0569
|  | 1:30:pm | 27 | 4.2 | 359 | 7.6 | 2.7 | 366 | 9.5 | 362 | 7.8 | 28.5 | 364 | 29.6 | 373 | 7.9 | 100 | 363 | 36 |  |  |  | 71.5 | 90.5263
Sunday | 2010-05-10 | 9:30:am | 23 | 4.9 | 348 | 7.3 | 4 | 362 | 19.6 | 351 | 7.6 | 68 | 360 | 71.2 | 355 | 7.8 | 118 | 348 | 100 | 2400 | 47 | 13000 | 42.3729 | 94.1176
|  | 11:30:am | 25 | 4.5 | 351 | 7.4 | 3.6 | 366 | 15.3 | 356 | 7.7 | 62 | 362 | 61.8 | 359 | 7.9 | 110 | 353 | 95 |  |  |  | 43.6364 | 94.1935
|  | 1:30:pm | 26 | 4.2 | 355 | 7.5 | 3 | 369 | 11.7 | 359 | 7.8 | 45 | 367 | 52.7 | 362 | 7.9 | 99 | 356 | 88 |  |  |  | 54.5455 | 93.3333
Monday | 2010-05-11 | 9:30:am | 24 | 4.8 | 347 | 7.3 | 4.5 | 340 | 14 | 352 | 7.7 | 25.3 | 342 | 36 | 357 | 7.9 | 127 | 342 | 95 | 2550 | 49 | 12500 | 80.0787 | 82.2134
|  | 11:30:am | 26 | 4.4 | 354 | 7.5 | 4 | 345 | 11 | 358 | 7.8 | 21.7 | 348 | 28 | 362 | 8 | 134 | 345 | 83 |  |  |  | 83.806 | 81.5668
|  | 1:30:pm | 28 | 4.2 | 357 | 7.6 | 3.6 | 348 | 9 | 362 | 7.9 | 18.5 | 353 | 22 | 366 | 8 | 138 | 351 | 72 |  |  |  | 86.5942 | 80.5405
Tuesday | 2010-05-12 | 9:30:am | 24 | 4.4 | 352 | 7.3 | 4.5 | 352 | 8 | 355 | 7.5 | 35.5 | 354 | 28 | 358 | 7.9 | 136 | 344 | 45 | 2250 | 47 | 13000 | 73.8971 | 87.3239
|  | 11:30:am | 26 | 4.2 | 355 | 7.4 | 3.8 | 355 | 6 | 359 | 7.6 | 29.6 | 350 | 24 | 363 | 7.9 | 144 | 348 | 38 |  |  |  | 79.4444 | 87.1622
|  | 1:30:pm | 28 | 4 | 357 | 7.5 | 3.2 | 359 | 9 | 361 | 7.7 | 22.6 | 352 | 22 | 366 | 8 | 137 | 351 | 33 |  |  |  | 83.5036 | 85.8407
Wednesday | 2010-05-13 | 9:30:am | 24 | 4.8 | 351 | 7.4 | 4.5 | 342 | 9 | 353 | 7.7 | 34.9 | 340 | 27 | 357 | 7.8 | 104 | 340 | 39 | 2400 | 48 | 13000 | 66.4423 | 87.106
|  | 11:30:am | 27 | 4.4 | 357 | 7.5 | 3.6 | 347 | 7 | 359 | 7.8 | 27.5 | 336 | 24 | 362 | 7.9 | 110 | 333 | 31 |  |  |  | 75 | 86.9091
|  | 1:30:pm | 29 | 4.2 | 359 | 7.6 | 3 | 350 | 6 | 363 | 7.9 | 22.7 | 331 | 21 | 367 | 7.9 | 116 | 328 | 24 |  |  |  | 80.431 | 86.7841
Thursday | 2010-05-14 | 9:30:am | 25 | 4.6 | 355 | 7.3 | 3.9 | 352 | 11 | 358 | 7.5 | 28.6 | 348 | 24 | 361 | 7.7 | 99 | 344 | 34 | 2550 | 49 | 12500 | 71.1111 | 86.3636
|  | 11:30:am | 27 | 4.3 | 357 | 7.4 | 3 | 358 | 9 | 361 | 7.6 | 23.7 | 353 | 20 | 363 | 7.8 | 105 | 347 | 28 |  |  |  | 77.4286 | 87.3418
|  | 1:30:pm | 29 | 4 | 360 | 7.5 | 2.7 | 361 | 8 | 363 | 7.7 | 19.6 | 358 | 18 | 368 | 7.9 | 112 | 351 | 24 |  |  |  | 82.5 | 86.2245
Friday | 2010-05-15 | 9:30:am | 26 | 4.8 | 351 | 7.4 | 4 | 358 | 9 | 355 | 7.5 | 23.8 | 352 | 29 | 359 | 7.8 | 118 | 347 | 45 | 2400 | 48 | 12500 | 79.8305 | 83.1933
|  | 11:30:am | 28 | 4.6 | 354 | 7.5 | 3.4 | 361 | 10 | 358 | 7.6 | 21.6 | 357 | 25 | 363 | 7.9 | 123 | 352 | 36 |  |  |  | 82.439 | 84.2593
|  | 1:30:pm | 30 | 4.2 | 359 | 7.7 | 2.8 | 365 | 8 | 362 | 7.8 | 18.5 | 361 | 20 | 366 | 7.9 | 127 | 357 | 29 |  |  |  | 85.4331 | 84.8649
Saturday | 2010-05-16 | 9:30:am | 25 | 4.5 | 350 | 7.4 | 3.3 | 350 | 8 | 352 | 7.5 | 23 | 347 | 27 | 359 | 7.7 | 104 | 343 | 40 | 2700 | 47 | 13000 | 77.8846 | 85.6522
|  | 11:30:am | 27 | 4.2 | 353 | 7.5 | 3 | 354 | 6 | 357 | 7.6 | 20 | 350 | 23 | 363 | 7.8 | 115 | 351 | 49 |  |  |  | 82.6087 | 85
|  | 1:30:pm | 28 | 4 | 358 | 7.6 | 2.8 | 359 | 5 | 361 | 7.7 | 16 | 355 | 18 | 369 | 7.9 | 129 | 353 | 51 |  |  |  | 87.5969 | 82.5
Sunday | 2010-05-17 | 9:30:am | 25 | 4.7 | 347 | 7.4 | 4.3 | 332 | 11 | 338 | 7.7 | 76 | 338 | 25 | 349 | 7.9 | 159 | 340 | 55 | 3600 | 49 | 13000 | 52.2013 | 94.3421
|  | 11:30:am | 27 | 4.2 | 351 | 7.5 | 4 | 337 | 9 | 343 | 7.8 | 65 | 345 | 22 | 353 | 8 | 145 | 347 | 42 |  |  |  | 55.1724 | 93.8462
|  | 1:30:pm | 29 | 4 | 356 | 7.6 | 3.8 | 343 | 7 | 348 | 7.8 | 53 | 351 | 16 | 359 | 8 | 133 | 356 | 38 |  |  |  | 60.1504 | 92.8302
Monday | 2010-05-18 | 9:30:am | 24 | 5 | 352 | 7.3 | 3.8 | 332 | 13 | 336 | 7.6 | 49 | 336 | 31 | 345 | 7.8 | 121 | 338 | 63 | 2700 | 50 | 12500 | 59.5041 | 92.2449
|  | 11:30:am | 25 | 4.6 | 347 | 7.4 | 3 | 339 | 11 | 342 | 7.7 | 37 | 342 | 26 | 353 | 7.9 | 126 | 342 | 55 |  |  |  | 70.6349 | 91.8919
|  | 1:30:pm | 27 | 4.2 | 355 | 7.5 | 2.6 | 346 | 9 | 349 | 7.8 | 31 | 348 | 19 | 359 | 8 | 138 | 348 | 44 |  |  |  | 77.5362 | 91.6129
Tuesday | 2010-05-19 | 9:30:am | 23 | 4.6 | 351 | 7.4 | 3.8 | 334 | 10 | 354 | 7.6 | 31 | 336 | 25 | 358 | 7.9 | 228 | 332 | 59 | 3750 | 47 | 12000 | 86.4035 | 87.7419
|  | 11:30:am | 25 | 4.3 | 355 | 7.5 | 3.3 | 339 | 8 | 358 | 7.7 | 27 | 338 | 21 | 362 | 8 | 199 | 335 | 44 |  |  |  | 86.4322 | 87.7778
|  | 1:30:pm | 26 | 4 | 358 | 7.6 | 2.7 | 343 | 6 | 361 | 7.8 | 23 | 340 | 17 | 366 | 8 | 184 | 338 | 38 |  |  |  | 87.5 | 88.2609
Wednesday | 2010-05-20 | 9:30:am | 24 | 4.8 | 351 | 7.2 | 4.3 | 338 | 13 | 354 | 7.5 | 35.4 | 342 | 26 | 358 | 7.7 | 184 | 336 | 45 | 3600 | 49 | 13000 | 80.7609 | 87.8531
|  | 11:30:am | 26 | 4.4 | 355 | 7.3 | 3.7 | 342 | 11 | 358 | 7.6 | 31.8 | 345 | 22 | 363 | 7.8 | 178 | 340 | 37 |  |  |  | 82.1348 | 88.3648
|  | 1:30:pm | 27 | 4.2 | 359 | 7.4 | 3 | 346 | 9 | 362 | 7.7 | 27.8 | 348 | 20 | 368 | 7.9 | 168 | 342 | 33 |  |  |  | 83.4524 | 89.2086
Thursday | 2010-05-21 | 9:30:am | 23 | 4.6 | 346 | 7.3 | 3.5 | 349 | 12 | 349 | 7.5 | 28.5 | 345 | 24 | 352 | 7.7 | 111 | 343 | 45 | 2700 | 47 | 13000 | 74.3243 | 87.7193
|  | 11:30:am | 25 | 4.3 | 349 | 7.4 | 3 | 355 | 10 | 353 | 7.6 | 23.4 | 350 | 20 | 357 | 7.8 | 99 | 346 | 36 |  |  |  | 76.3636 | 87.1795
|  | 1:30:pm | 26 | 4 | 351 | 7.5 | 2.7 | 358 | 9 | 356 | 7.7 | 20.5 | 353 | 16 | 359 | 7.9 | 95 | 350 | 32 |  |  |  | 78.4211 | 86.8293
Friday | 2010-05-22 | 9:30:am | 24 | 4.7 | 349 | 7.4 | 4 | 351 | 14 | 352 | 7.6 | 26 | 347 | 27 | 357 | 7.8 | 125 | 345 | 39 | 2850 | 48 | 12500 | 79.2 | 84.6154
|  | 11:30:am | 25 | 4.4 | 352 | 7.5 | 3.7 | 355 | 12 | 356 | 7.7 | 21 | 352 | 23 | 361 | 7.9 | 115 | 349 | 33 |  |  |  | 81.7391 | 82.381
|  | 1:30:pm | 27 | 4.2 | 355 | 7.6 | 3.2 | 358 | 10 | 359 | 7.8 | 16 | 356 | 18 | 366 | 8 | 110 | 352 | 27 |  |  |  | 85.4545 | 80
Saturday | 2010-05-23 | 9:30:am | 24 | 4.7 | 349 | 7.2 | 4.5 | 334 | 5.6 | 353 | 7.5 | 26.3 | 336 | 29.6 | 356 | 7.8 | 84 | 334 | 97.9 | 2100 | 45 | 12500 | 68.6905 | 82.8897
|  | 11:30:am | 26 | 4.3 | 353 | 7.3 | 3.8 | 338 | 6.9 | 358 | 7.6 | 22.8 | 337 | 23.5 | 360 | 7.9 | 99 | 336 | 88.5 |  |  |  | 76.9697 | 83.3333
|  | 1:30:pm | 28 | 4 | 357 | 7.4 | 3 | 342 | 8.5 | 363 | 7.7 | 18.3 | 340 | 21.9 | 365 | 8 | 107 | 338 | 77.4 |  |  |  | 82.8972 | 83.6066
Sunday | 2010-05-24 | 9:30:am | 22 | 4.6 | 346 | 7.3 | 4.7 | 332 | 15 | 349 | 7.5 | 83 | 338 | 29 | 353 | 7.7 | 149 | 342 | 76.8 | 3300 | 48 | 12500 | 44.2953 | 94.3373
|  | 11:30:am | 24 | 4.3 | 349 | 7.4 | 3.9 | 339 | 12 | 352 | 7.6 | 72 | 342 | 25 | 357 | 7.8 | 158 | 345 | 55.3 |  |  |  | 54.4304 | 94.5833
|  | 1:30:pm | 26 | 4 | 351 | 7.5 | 3.3 | 342 | 10 | 356 | 7.7 | 66 | 347 | 21 | 362 | 7.9 | 166 | 349 | 42.8 |  |  |  | 60.241 | 95
Monday | 2010-05-25 | 9:30:am | 23 | 4.8 | 348 | 7.2 | 3.9 | 338 | 11 | 353 | 7.5 | 38.4 | 343 | 27 | 357 | 7.7 | 154 | 348 | 66.9 | 2700 | 49 | 13000 | 75.0649 | 89.8438
|  | 11:30:am | 25 | 4.5 | 352 | 7.3 | 3.3 | 343 | 9 | 356 | 7.6 | 29.5 | 346 | 22 | 361 | 7.8 | 159 | 344 | 45.8 |  |  |  | 81.4465 | 88.8136
|  | 1:30:pm | 28 | 4.2 | 356 | 7.4 | 2.7 | 347 | 8 | 359 | 7.7 | 22.6 | 349 | 18 | 363 | 7.9 | 163 | 346 | 31.6 |  |  |  | 86.135 | 88.0531
Tuesday | 2010-05-26 | 9:30:am | 24 | 4.6 | 348 | 7.4 | 4.6 | 340 | 13 | 351 | 7.7 | 40 | 328 | 26 | 355 | 8 | 111 | 320 | 44 | 1200 | 48 | 12500 | 63.964 | 88.5
|  | 11:30:am | 25 | 4.3 | 350 | 7.5 | 4 | 342 | 11 | 355 | 7.8 | 35 | 333 | 22 | 359 | 7.9 | 123 | 326 | 37 |  |  |  | 71.5447 | 88.5714
|  | 1:30:pm | 27 | 4 | 352 | 7.6 | 3.7 | 347 | 9 | 358 | 7.9 | 28 | 339 | 21 | 362 | 7.9 | 114 | 329 | 31 |  |  |  | 75.4386 | 86.7857
Wednesday | 2010-05-27 | 9:30:am | 24 | 4.5 | 349 | 7.5 | 4.8 | 346 | 12 | 352 | 7.7 | 48.1 | 352 | 29 | 356 | 7.9 | 108 | 354 | 54 | 1650 | 47 | 12000 | 55.463 | 90.0208
|  | 11:30:am | 26 | 4.2 | 352 | 7.6 | 4.2 | 349 | 10 | 357 | 7.8 | 42.7 | 356 | 25 | 359 | 7.8 | 112 | 358 | 45 |  |  |  | 61.875 | 90.1639
|  | 1:30:pm | 29 | 4 | 355 | 7.7 | 3.8 | 354 | 8 | 359 | 7.9 | 36.8 | 358 | 20 | 364 | 8 | 119 | 361 | 38 |  |  |  | 69.0756 | 89.6739
Thursday | 2010-05-28 | 9:30:am | 27 | 4.3 | 348 | 7.3 | 3.8 | 348 | 15 | 352 | 7.5 | 27.5 | 345 | 25 | 357 | 7.8 | 88 | 342 | 38 | 1200 | 48 | 13000 | 68.75 | 86.1818
|  | 11:30:am | 29 | 4 | 351 | 7.4 | 3.2 | 352 | 12 | 357 | 7.6 | 23.6 | 348 | 21 | 361 | 7.9 | 73 | 346 | 33 |  |  |  | 67.6712 | 86.4407
|  | 1:30:pm | 31 | 4 | 357 | 7.5 | 2.8 | 358 | 10 | 362 | 7.7 | 21.5 | 352 | 18 | 367 | 8 | 62 | 350 | 31 |  |  |  | 65.3226 | 86.9767
Friday | 2010-05-29 | 9:30:am | 25 | 4.5 | 345 | 7.4 | 3.5 | 353 | 13 | 349 | 7.6 | 32.7 | 349 | 28 | 353 | 7.8 | 66 | 346 | 39 | 1400 | 49 | 12500 | 50.4545 | 89.2966
|  | 11:30:am | 27 | 4.3 | 347 | 7.5 | 3 | 357 | 11 | 353 | 7.7 | 27.4 | 352 | 23 | 359 | 7.8 | 52 | 349 | 34 |  |  |  | 47.3077 | 89.0511
|  | 1:30:pm | 28 | 4 | 349 | 7.6 | 2.4 | 359 | 9 | 359 | 7.8 | 23.6 | 356 | 18 | 363 | 7.9 | 59 | 352 | 30 |  |  |  | 60 | 89.8305
Saturday | 2010-05-30 | 9:30:am | 25 | 4.6 | 347 | 7.4 | 4.6 | 338 | 17 | 351 | 7.7 | 55 | 340 | 74 | 356 | 7.9 | 57.8 | 342 | 66.8 | 900 | 48 | 12500 | 4.8443 | 91.6364
|  | 11:30:am | 27 | 4.2 | 350 | 7.5 | 4.2 | 342 | 13 | 356 | 7.8 | 43 | 345 | 68 | 361 | 7.9 | 49.7 | 347 | 54.8 |  |  |  | 13.4809 | 90.2326
|  | 1:30:pm | 29 | 4 | 353 | 7.6 | 3.8 | 346 | 11 | 359 | 7.9 | 38 | 348 | 53 | 367 | 8 | 47.5 | 351 | 47.4 |  |  |  | 20 | 90
Sunday | 2010-05-31 | 9:30 | 26 | 4.3 | 348 | 7.3 | 4 | 334 | 14.4 | 351 | 7.7 | 46.3 | 338 | 63.6 | 355 | 7.8 | 44.2 | 334 | 64.8 | 750 | 49 | 13000 | -4.7511 | 91.3607
|  | 11:30 | 28 | 4 | 352 | 7.4 | 3.6 | 338 | 12.3 | 356 | 7.8 | 35.8 | 343 | 43.6 | 359 | 7.9 | 49.5 | 339 | 55.7 |  |  |  | 27.6768 | 89.9441
|  | 1:30:pm | 30 | 4 | 356 | 7.5 | 3 | 343 | 10.5 | 360 | 7.9 | 28.5 | 349 | 39.5 | 363 | 8 | 55.3 | 345 | 43.8 |  |  |  | 48.4629 | 89.4737

## 6
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-06-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr)
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | S-R | S-SUP
Saturday | 2010-06-01 | 9:30:am | 26 | 4 | 348 | 7.4 | 4.2 | 328 | 11 | 352 | 7.7 | 31.6 | 338 | 27 | 356 | 7.9 | 39 | 332 | 23 | 450 | 54 | 12500 | 18.9744 | 86.7089
|  | 11:30:am | 28 | 4.2 | 353 | 7.5 | 3.8 | 334 | 10 | 357 | 7.8 | 27.5 | 342 | 23 | 362 | 7.9 | 35 | 336 | 21 |  |  |  | 21.4286 | 86.1818
|  | 1:30:pm | 30 | 4 | 356 | 7.6 | 4.8 | 338 | 9 | 361 | 7.9 | 22.7 | 346 | 20 | 367 | 8 | 38 | 339 | 19 |  |  |  | 40.2632 | 78.8546
Saturday | 2010-06-02 | 9:30:am | 26 | 4 | 352 | 7.3 | 3.9 | 330 | 14 | 356 | 7.6 | 77 | 332 | 29 | 359 | 7.7 | 116 | 328 | 45 | 2700 | 58 | 13000 | 33.6207 | 94.9351
|  | 11:30:am | 29 | 4 | 356 | 7.4 | 3.2 | 335 | 11 | 359 | 7.7 | 63 | 334 | 25 | 363 | 7.8 | 100 | 333 | 39 |  |  |  | 37 | 94.9206
|  | 1:30:pm | 31 | 4.2 | 358 | 7.5 | 2.6 | 339 | 10 | 363 | 7.8 | 45 | 338 | 22 | 369 | 7.9 | 94 | 335 | 36 |  |  |  | 52.1277 | 94.2222
Sunday | 2010-06-03 | 9:30:am | 27 | 4 | 346 | 7.3 | 4.8 | 336 | 16 | 349 | 7.6 | 44 | 334 | 34 | 352 | 7.8 | 52 | 334 | 48 | 2500 | 59 | 13000 | 15.3846 | 89.0909
|  | 11:30:am | 29 | 4.2 | 349 | 7.4 | 4 | 342 | 12 | 353 | 7.7 | 40 | 338 | 29 | 357 | 7.9 | 58 | 337 | 44 |  |  |  | 31.0345 | 90
|  | 1:30:pm | 32 | 4.2 | 353 | 7.5 | 3.3 | 346 | 11 | 358 | 7.8 | 37 | 342 | 26 | 362 | 8 | 55 | 338 | 38 |  |  |  | 32.7273 | 91.0811
Monday | 2010-06-04 | 9:30:am | 28 | 4.5 | 348 | 7.4 | 3 | 352 | 16 | 352 | 7.6 | 28 | 348 | 29 | 356 | 7.8 | 44 | 345 | 33 | 1350 | 56 | 12500 | 36.3636 | 89.2857
|  | 11:30:am | 30 | 4.2 | 353 | 7.5 | 2.6 | 358 | 12 | 356 | 7.7 | 25 | 354 | 24 | 361 | 7.9 | 41 | 347 | 28 |  |  |  | 39.0244 | 89.6
|  | 1:30:pm | 33 | 4 | 356 | 7.6 | 2.2 | 361 | 10 | 359 | 7.8 | 22 | 359 | 20 | 366 | 7.9 | 37 | 352 | 25 |  |  |  | 40.5405 | 90
Tuesday | 2010-06-05 | 9:30:am | 29 | 4.6 | 348 | 7.5 | 4.2 | 337 | 12 | 352 | 7.7 | 28 | 336 | 25 | 356 | 7.9 | 55 | 334 | 27 | 1400 | 58 | 13000 | 49.0909 | 85
|  | 11:30:am | 32 | 4.3 | 354 | 7.6 | 3.8 | 342 | 10 | 355 | 7.8 | 25 | 339 | 27 | 357 | 7.9 | 45 | 338 | 23 |  |  |  | 44.4444 | 84.8
|  | 1:30:pm | 34 | 4 | 359 | 7.7 | 3.3 | 345 | 9 | 362 | 7.9 | 22 | 342 | 29 | 362 | 8 | 48 | 342 | 20 |  |  |  | 54.1667 | 85
Wednesday | 2010-06-06 | 9:30:am | 27 | 4.7 | 352 | 7.3 | 4 | 330 | 13.6 | 356 | 7.5 | 49.7 | 336 | 29 | 359 | 7.7 | 122 | 334 | 29 | 2700 | 56 | 13000 | 59.2623 | 91.9517
|  | 11:30:am | 29 | 4.5 | 355 | 7.4 | 3.5 | 336 | 11.8 | 359 | 7.6 | 44.3 | 339 | 26 | 365 | 7.8 | 115 | 338 | 22 |  |  |  | 61.4783 | 92.0993
|  | 1:30:pm | 31 | 4.2 | 359 | 7.5 | 3.2 | 339 | 9.4 | 364 | 7.7 | 37.4 | 341 | 23 | 369 | 7.9 | 107 | 341 | 20 |  |  |  | 65.0467 | 91.4439
Thursday | 2010-06-07 | 9:30:am | 26 | 5 | 356 | 7.3 | 4.8 | 330 | 17.5 | 361 | 7.5 | 70 | 332 | 32 | 366 | 7.7 | 103 | 330 | 39 | 2250 | 59 | 13000 | 32.0388 | 93.1429
|  | 11:30:am | 28 | 4.7 | 359 | 7.4 | 4.5 | 333 | 14.3 | 366 | 7.6 | 61 | 338 | 27 | 369 | 7.8 | 97 | 332 | 43 |  |  |  | 37.1134 | 92.623
|  | 1:30:pm | 30 | 4.4 | 363 | 7.5 | 4 | 337 | 12.3 | 368 | 7.7 | 55 | 339 | 25 | 373 | 7.9 | 90 | 335 | 48 |  |  |  | 38.8889 | 92.7273
Friday | 2010-06-08 | 9:30:am | 27 | 5 | 355 | 7.3 | 4.3 | 336 | 13 | 358 | 7.6 | 61 | 334 | 29 | 361 | 7.7 | 151 | 328 | 45 | 2700 | 58 | 12500 | 59.6026 | 92.9508
|  | 11:30:am | 29 | 4.5 | 357 | 7.4 | 4 | 340 | 11 | 360 | 7.7 | 53 | 337 | 25 | 365 | 7.8 | 135 | 331 | 38 |  |  |  | 60.7407 | 92.4528
|  | 1:30:pm | 32 | 4.2 | 361 | 7.5 | 3.6 | 343 | 9 | 364 | 7.8 | 41 | 340 | 22 | 369 | 7.9 | 122 | 336 | 33 |  |  |  | 66.3934 | 91.2195
Saturday | 2010-06-09 | 9:30:am | 27 | 4.5 | 348 | 7.3 | 3.8 | 326 | 13 | 352 | 7.5 | 36.8 | 332 | 31 | 356 | 7.6 | 87 | 332 | 36 | 1650 | 57 | 12500 | 57.7011 | 89.6739
|  | 11:30:am | 30 | 4.2 | 352 | 7.4 | 3 | 330 | 11 | 357 | 7.6 | 39.4 | 337 | 28 | 360 | 7.7 | 92 | 338 | 33 |  |  |  | 57.1739 | 92.3858
|  | 1:30:pm | 33 | 4 | 355 | 7.5 | 2.7 | 332 | 9 | 361 | 7.7 | 41.7 | 341 | 26 | 366 | 7.8 | 99 | 342 | 28 |  |  |  | 57.8788 | 93.5252
Sunday | 2010-06-10 | 9:30:am | 28 | 4.6 | 349 | 7.4 | 3.3 | 333 | 14 | 353 | 7.6 | 29 | 345 | 29 | 358 | 7.8 | 43 | 349 | 36 | 1050 | 59 | 12500 | 32.5581 | 88.6207
|  | 11:30:am | 32 | 4.3 | 352 | 7.5 | 3 | 338 | 11 | 356 | 7.7 | 24 | 338 | 26 | 359 | 7.9 | 47 | 344 | 32 |  |  |  | 48.9362 | 87.5
|  | 1:30:pm | 35 | 4 | 357 | 7.6 | 2.6 | 342 | 9 | 359 | 7.8 | 20 | 335 | 22 | 363 | 7.9 | 52 | 340 | 28 |  |  |  | 61.5385 | 87
Monday | 2010-06-11 | 9:30:am | 27 | 4.5 | 355 | 7.3 | 4.3 | 337 | 13 | 358 | 7.5 | 33 | 349 | 32 | 363 | 7.7 | 59 | 343 | 43 | 1200 | 57 | 13000 | 44.0678 | 86.9697
|  | 11:30:am | 29 | 4.3 | 359 | 7.4 | 3.5 | 344 | 11 | 362 | 7.6 | 27 | 338 | 28 | 367 | 7.8 | 63 | 337 | 38 |  |  |  | 57.1429 | 87.037
|  | 1:30:pm | 31 | 4 | 361 | 7.5 | 3 | 348 | 8 | 366 | 7.7 | 22 | 331 | 26 | 370 | 7.9 | 69 | 330 | 31 |  |  |  | 68.1159 | 86.3636
Tuesday | 2010-06-12 | 9:30:am | 28 | 4.2 | 359 | 7.3 | 4 | 334 | 12 | 362 | 7.5 | 33.8 | 326 | 27 | 366 | 7.7 | 87 | 326 | 44 | 2100 | 58 | 12500 | 61.1494 | 88.1657
|  | 11:30:am | 32 | 4 | 364 | 7.4 | 3.3 | 336 | 10 | 369 | 7.6 | 27.4 | 330 | 23 | 371 | 7.8 | 93 | 328 | 40 |  |  |  | 70.5376 | 87.9562
|  | 1:30:pm | 36 | 4 | 366 | 7.5 | 2.7 | 340 | 7 | 370 | 7.7 | 21.5 | 333 | 20 | 377 | 7.9 | 99 | 330 | 37 |  |  |  | 78.2828 | 87.4419
Wednesday | 2010-06-13 | 9:30:am | 27 | 4 | 400 | 7.6 | 3.5 | 338 | 8 | 406 | 7.7 | 18.9 | 336 | 34.8 | 411 | 7.8 | 39.4 | 334 | 38.4 | 750 | 55 | 13000 | 52.0305 | 81.4815
|  | 11:30:am | 30 | 4 | 405 | 7.7 | 2.9 | 345 | 7 | 410 | 7.8 | 16.4 | 338 | 28.6 | 417 | 7.9 | 36.3 | 335 | 32.9 |  |  |  | 54.8209 | 82.3171
|  | 1:30:pm | 32 | 4 | 411 | 7.8 | 2.3 | 347 | 5 | 417 | 7.9 | 15.4 | 342 | 23.7 | 421 | 8 | 33.4 | 338 | 27.4 |  |  |  | 53.8922 | 85.0649
Thursday | 2010-06-14 | 9:30:am | 28 | 4.2 | 412 | 7.3 | 4.2 | 330 | 12 | 420 | 7.5 | 33 | 332 | 25 | 425 | 7.7 | 40.2 | 330 | 29 | 1050 | 58 | 13000 | 17.9104 | 87.2727
|  | 11:30:am | 31 | 4 | 420 | 7.4 | 3.8 | 336 | 9 | 424 | 7.6 | 27 | 334 | 21 | 431 | 7.8 | 44.3 | 332 | 24 |  |  |  | 39.0519 | 85.9259
|  | 1:30:pm | 33 | 4 | 425 | 7.5 | 3 | 339 | 7 | 428 | 7.7 | 23 | 337 | 18 | 437 | 7.9 | 39.6 | 334 | 21 |  |  |  | 41.9192 | 86.9565
Friday | 2010-06-15 | 9:30:am | 30 | 4.2 | 342 | 7.5 | 4.6 | 328 | 16 | 346 | 7.8 | 33.5 | 332 | 27 | 350 | 8 | 35.8 | 334 | 23 | 750 | 56 | 12500 | 6.4246 | 86.2687
|  | 11:30:am | 34 | 4 | 346 | 7.6 | 4 | 333 | 12 | 349 | 7.8 | 34 | 330 | 22 | 354 | 8 | 38.4 | 332 | 20 |  |  |  | 11.4583 | 88.2353
|  | 1:30:pm | 37 | 4 | 349 | 7.7 | 3.6 | 336 | 10 | 353 | 7.9 | 37 | 332 | 20 | 358 | 8.3 | 42.8 | 330 | 16 |  |  |  | 13.5514 | 90.2703
Saturday | 2010-06-16 | 9:30:am | 28 | 4.3 | 347 | 7.4 | 3.9 | 332 | 15 | 355 | 7.7 | 56 | 332 | 29 | 359 | 7.8 | 100 | 330 | 45 | 2250 | 58 | 13000 | 44 | 93.0357
|  | 11:30:am | 32 | 4 | 352 | 7.5 | 3 | 335 | 11 | 358 | 7.8 | 43 | 333 | 24 | 363 | 7.9 | 90 | 332 | 39 |  |  |  | 52.2222 | 93.0233
|  | 1:30:pm | 35 | 4 | 354 | 7.6 | 2.7 | 338 | 10 | 362 | 7.9 | 37 | 335 | 22 | 369 | 8 | 83 | 333 | 33 |  |  |  | 55.4217 | 92.7027
Sunday | 2010-06-17 | 9:30:am | 27 | 4.4 | 397 | 7.5 | 3.9 | 346 | 13 | 407 | 7.7 | 62 | 342 | 27 | 412 | 7.8 | 72 | 340 | 33 | 1250 | 59 | 12500 | 13.8889 | 93.7097
|  | 11:30:am | 29 | 4.2 | 406 | 7.6 | 3.5 | 349 | 11 | 413 | 7.8 | 53 | 345 | 23 | 416 | 7.9 | 77 | 342 | 28 |  |  |  | 31.1688 | 93.3962
|  | 1:30:pm | 31 | 4 | 412 | 7.7 | 3 | 351 | 8 | 420 | 7.9 | 48 | 348 | 21 | 423 | 8 | 69 | 346 | 25 |  |  |  | 30.4348 | 93.75
Monday | 2010-06-18 | 9:30:am | 29 | 4.5 | 442 | 7.4 | 3 | 339 | 16 | 446 | 7.6 | 29.6 | 336 | 25 | 449 | 7.8 | 42 | 333 | 29 | 1050 | 57 | 13000 | 29.5238 | 89.8649
|  | 11:30:am | 32 | 4.2 | 446 | 7.5 | 2.8 | 342 | 13 | 449 | 7.7 | 25.4 | 339 | 22 | 452 | 7.9 | 45 | 336 | 26 |  |  |  | 43.5556 | 88.9764
|  | 1:30:pm | 35 | 4 | 449 | 7.6 | 2.5 | 345 | 11 | 452 | 7.8 | 24.4 | 342 | 20 | 456 | 7.9 | 41 | 338 | 24 |  |  |  | 40.4878 | 89.7541
Tuesday | 2010-06-19 | 9:30:am | 27 | 4.7 | 398 | 7.6 | 3.8 | 338 | 9 | 405 | 7.7 | 35.3 | 336 | 29 | 411 | 7.9 | 38.5 | 333 | 33 | 900 | 58 | 13000 | 8.3117 | 89.2351
|  | 11:30:am | 29 | 4.3 | 404 | 7.7 | 3.3 | 336 | 10 | 411 | 7.8 | 37.4 | 334 | 25 | 421 | 7.9 | 41.2 | 331 | 28 |  |  |  | 9.2233 | 91.1765
|  | 1:30:pm | 31 | 4.2 | 412 | 7.8 | 2.7 | 334 | 8 | 417 | 7.9 | 39 | 331 | 22 | 423 | 8 | 45.3 | 328 | 24 |  |  |  | 13.9073 | 93.0769
Wednesday | 2010-06-20 | 9:30:am | 29 | 4.8 | 449 | 7.7 | 4 | 328 | 13 | 452 | 7.8 | 32.7 | 332 | 26 | 457 | 7.9 | 38.4 | 336 | 34 | 750 | 59 | 13000 | 14.8438 | 87.7676
|  | 11:30:am | 31 | 4.4 | 451 | 7.8 | 3.7 | 333 | 11 | 455 | 7.8 | 37.8 | 336 | 22 | 462 | 7.9 | 44.2 | 339 | 29 |  |  |  | 14.4796 | 90.2116
|  | 1:30:pm | 33 | 4.7 | 453 | 7.9 | 3.2 | 338 | 9 | 458 | 7.9 | 34.5 | 334 | 19 | 466 | 8 | 48.5 | 341 | 27 |  |  |  | 28.866 | 90.7246
Thursday | 2010-06-21 | 9:30:am | 27 | 4 | 339 | 7.1 | 4 | 326 | 12 | 342 | 7.3 | 33.2 | 330 | 25 | 348 | 7.5 | 35.2 | 336 | 32 | 300 | 57 | 13000 | 5.6818 | 87.9518
|  | 11:30:am | 29 | 4 | 342 | 7.2 | 3.3 | 333 | 9 | 348 | 7.4 | 27.4 | 324 | 26 | 353 | 7.6 | 37.4 | 339 | 27 |  |  |  | 26.738 | 87.9562
|  | 1:30:pm | 31 | 4 | 347 | 7.3 | 2.7 | 337 | 7 | 353 | 7.5 | 22.6 | 331 | 28 | 356 | 7.7 | 42.6 | 342 | 22 |  |  |  | 46.9484 | 88.0531
Friday | 2010-06-22 | 9:30:am | 29 | 4.2 | 342 | 7.2 | 3.6 | 338 | 10 | 347 | 7.5 | 35.5 | 336 | 28 | 342 | 7.7 | 36.5 | 332 | 28 | _ | 50 | 10000 | 2.7397 | 89.8592
|  | 11:30:am | 32 | 4 | 346 | 7.3 | 3 | 342 | 8 | 352 | 7.6 | 31.6 | 334 | 23 | 347 | 7.8 | 42.7 | 336 | 24 |  |  |  | 25.9953 | 90.5063
|  | 1:30:pm | 34 | 4 | 349 | 7.4 | 2.6 | 347 | 6 | 356 | 7.7 | 28.6 | 338 | 21 | 352 | 7.9 | 44.8 | 337 | 20 |  |  |  | 36.1607 | 90.9091
Saturday | 2010-06-23 | 9:30:am | 29 | 4.3 | 345 | 7.1 | 3.5 | 338 | 10 | 348 | 7.3 | 33.1 | 334 | 25 | 352 | 7.6 | 80 | 336 | 29 | 750 | 59 | 13000 | 58.625 | 89.426
|  | 11:30:am | 33 | 4 | 349 | 7.2 | 3 | 343 | 8 | 353 | 7.4 | 30.4 | 337 | 21 | 356 | 7.7 | 73 | 338 | 24 |  |  |  | 58.3562 | 90.1316
|  | 1:30:pm | 36 | 4 | 353 | 7.3 | 2.7 | 346 | 6 | 358 | 7.5 | 28.5 | 341 | 18 | 360 | 7.8 | 60 | 341 | 20 |  |  |  | 52.5 | 90.5263
Sunday | 2010-06-24 | 9:30:am | 28 | 4.4 | 344 | 7.2 | 3.6 | 336 | 11 | 348 | 7.4 | 25 | 339 | 22 | 351 | 7.6 | 28 | 336 | 22 | _ | 58 | 13000 | 10.7143 | 85.6
|  | 11:30:am | 30 | 4.2 | 348 | 7.3 | 3 | 341 | 9 | 352 | 7.5 | 22 | 343 | 19 | 354 | 7.7 | 25 | 338 | 19 |  |  |  | 12 | 86.3636
|  | 1:30:pm | 32 | 4 | 352 | 7.4 | 2.7 | 344 | 7 | 356 | 7.6 | 20 | 348 | 15 | 359 | 7.8 | 22 | 342 | 16 |  |  |  | 9.0909 | 86.5
Monday | 2010-06-25 | 9:30:am | 27 | 4.6 | 349 | 7.3 | 3 | 345 | 13 | 352 | 7.5 | 28 | 341 | 27 | 356 | 7.6 | 31 | 337 | 28 | _ | 57 | 12000 | 9.6774 | 89.2857
|  | 11:30:am | 29 | 4.3 | 353 | 7.4 | 2.6 | 351 | 11 | 356 | 7.6 | 26 | 344 | 23 | 359 | 7.7 | 29 | 341 | 25 |  |  |  | 10.3448 | 90
|  | 1:30:pm | 31 | 4 | 356 | 7.5 | 2.2 | 356 | 9 | 359 | 7.7 | 23 | 349 | 20 | 362 | 7.8 | 27 | 345 | 21 |  |  |  | 14.8148 | 90.4348
Tuesday | 2010-06-26 | 9:30:am | 30 | 4.8 | 352 | 7.4 | 3.8 | 338 | 14 | 355 | 7.6 | 28 | 335 | 25 | 358 | 7.8 | 32 | 332 | 29 | _ | 60 | 12500 | 12.5 | 86.4286
|  | 11:30:am | 32 | 4.5 | 357 | 7.5 | 3.3 | 342 | 12 | 361 | 7.7 | 24 | 338 | 22 | 363 | 7.9 | 29 | 336 | 24 |  |  |  | 17.2414 | 86.25
|  | 1:30:pm | 34 | 4.2 | 362 | 7.6 | 2.9 | 346 | 10 | 366 | 7.8 | 21 | 342 | 19 | 369 | 8 | 25 | 338 | 20 |  |  |  | 16 | 86.1905
Wednesday | 2010-06-27 | 9:30:am | 27 | 4 | 355 | 7.3 | 3 | 335 | 11 | 360 | 7.5 | 30 | 333 | 23 | 363 | 7.7 | 33 | 330 | 30 | _ | 58 | 13000 | 9.0909 | 90
|  | 11:30:am | 29 | 4 | 359 | 7.4 | 2.6 | 338 | 9 | 363 | 7.6 | 26 | 336 | 21 | 367 | 7.8 | 27 | 332 | 26 |  |  |  | 3.7037 | 90
|  | 1:30:pm | 31 | 4 | 361 | 7.5 | 2 | 342 | 6 | 366 | 7.7 | 22 | 341 | 17 | 371 | 7.9 | 25 | 336 | 22 |  |  |  | 12 | 90.9091
Thursday | 2010-06-28 | 9:30:am | 28 | 4.3 | 344 | 7.4 | 2.8 | 329 | 9 | 347 | 7.6 | 22 | 326 | 19 | 351 | 7.7 | 25 | 323 | 16 | _ | 56 | 13000 | 12 | 87.2727
|  | 11:30:am | 32 | 4 | 347 | 7.5 | 2.5 | 325 | 7 | 351 | 7.7 | 20 | 322 | 16 | 356 | 7.8 | 23 | 320 | 12 |  |  |  | 13.0435 | 87.5
|  | 1:30:pm | 35 | 4 | 349 | 7.6 | 2.2 | 321 | 6 | 355 | 7.8 | 17 | 318 | 12 | 360 | 7.9 | 20 | 316 | 11 |  |  |  | 15 | 87.0588
Friday | 2010-06-29 | 9:30:am | 27 | 4.6 | 343 | 7.3 | 3.3 | 327 | 11 | 346 | 7.5 | 19 | 323 | 13 | 359 | 7.6 | 23 | 319 | 19 | _ | 58 | 12500 | 17.3913 | 82.6316
|  | 11:30:am | 30 | 4.3 | 346 | 7.4 | 2.7 | 324 | 8 | 350 | 7.6 | 16 | 321 | 11 | 362 | 7.7 | 20 | 316 | 12 |  |  |  | 20 | 83.125
|  | 1:30:pm | 33 | 4 | 351 | 7.5 | 2.3 | 320 | 7 | 353 | 7.7 | 13 | 317 | 9 | 366 | 7.8 | 18 | 312 | 10 |  |  |  | 27.7778 | 82.3077
Saturday | 2010-06-30 | 9:30:am | 29 | 4.4 | 354 | 7.5 | 3.8 | 321 | 8 | 356 | 7.6 | 20 | 318 | 18 | 359 | 7.7 | 24 | 314 | 21 | _ | 60 | 12500 | 16.6667 | 81
|  | 11:30:am | 33 | 4.2 | 357 | 7.6 | 3.5 | 317 | 6 | 359 | 7.7 | 16 | 314 | 15 | 362 | 7.8 | 21 | 310 | 16 |  |  |  | 23.8095 | 78.125
|  | 1:30:pm | 37 | 4 | 359 | 7.7 | 3 | 311 | 5 | 363 | 7.8 | 14 | 310 | 12 | 366 | 7.9 | 17 | 307 | 12 |  |  |  | 17.6471 | 78.5714
[23 empty] | #DIV/0! | #DIV/0!
[23 empty] | #DIV/0! | #DIV/0!
[23 empty] | #DIV/0! | #DIV/0!

## 7
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-07-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr)
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | S-R | S-SUP
Saturday | 2010-07-01 | 9:30:am | 29 | 4.4 | 333 | 7.3 | 3.3 | 289 | 7 | 335 | 7.4 | 18 | 284 | 16 | 338 | 7.5 | 23 | 280 | 17 | _ | 54 | 12500 | 21.7391 | 81.6667
|  | 11:30:am | 32 | 4.2 | 330 | 7.4 | 3 | 280 | 5 | 331 | 7.5 | 12 | 278 | 11 | 335 | 7.6 | 20 | 274 | 15 |  |  |  | 40 | 75
|  | 1:30:pm | 36 | 4 | 322 | 7.5 | 2.7 | 276 | 3 | 327 | 7.6 | 11 | 273 | 9 | 330 | 7.7 | 18 | 268 | 13 |  |  |  | 38.8889 | 75.4545
Saturday | 2010-07-02 | 9:30:am | 32 | 4.6 | 336 | 7.4 | 2.8 | 278 | 8 | 333 | 7.5 | 19 | 276 | 18 | 339 | 7.7 | 25 | 270 | 23 | _ | 58 | 13000 | 24 | 85.2632
|  | 11:30:am | 34 | 4.3 | 331 | 7.5 | 2.3 | 272 | 4 | 328 | 7.6 | 16 | 270 | 14 | 333 | 7.8 | 21 | 263 | 20 |  |  |  | 23.8095 | 85.625
|  | 1:30:pm | 37 | 4 | 329 | 7.6 | 2 | 268 | 2 | 322 | 7.7 | 13 | 263 | 11 | 324 | 7.9 | 18 | 260 | 17 |  |  |  | 27.7778 | 84.6154
Sunday | 2010-07-03 | 9:30:am | 28 | 4 | 321 | 7.5 | 3.7 | 279 | 9 | 318 | 7.6 | 22 | 274 | 20 | 315 | 7.7 | 29 | 271 | 25 | _ | 59 | 13000 | 24.1379 | 83.1818
|  | 11:30:am | 31 | 4 | 318 | 7.6 | 3.2 | 272 | 7 | 316 | 7.7 | 18 | 267 | 16 | 310 | 7.8 | 26 | 268 | 22 |  |  |  | 30.7692 | 82.2222
|  | 1:30:pm | 33 | 4 | 312 | 7.7 | 3 | 267 | 4 | 310 | 7.8 | 15 | 262 | 13 | 306 | 7.9 | 22 | 263 | 18 |  |  |  | 31.8182 | 80
Monday | 2010-07-04 | 9:30:am | 30 | 4.4 | 314 | 7.4 | 2.7 | 278 | 8 | 311 | 7.5 | 23 | 274 | 21 | 307 | 7.7 | 33 | 270 | 28 | 750 | 56 | 12500 | 30.303 | 88.2609
|  | 11:30:am | 33 | 4.2 | 310 | 7.5 | 2.3 | 283 | 6 | 308 | 7.6 | 20 | 280 | 19 | 300 | 7.8 | 38 | 264 | 25 |  |  |  | 47.3684 | 88.5
|  | 1:30:pm | 37 | 4 | 305 | 7.6 | 2 | 288 | 4 | 302 | 7.7 | 18 | 285 | 16 | 296 | 7.9 | 42 | 278 | 22 |  |  |  | 57.1429 | 88.8889
Tuesday | 2010-07-05 | 9:30:am | 33 | 4.4 | 321 | 7.3 | 3.3 | 288 | 6 | 326 | 7.4 | 20 | 284 | 18 | 328 | 7.5 | 23 | 280 | 20 | _ | 58 | 13000 | 13.0435 | 83.5
|  | 11:30:am | 36 | 4.2 | 325 | 7.4 | 2.7 | 279 | 4 | 328 | 7.5 | 17 | 277 | 15 | 331 | 7.6 | 20 | 273 | 18 |  |  |  | 15 | 84.1176
|  | 1:30:pm | 39 | 4 | 329 | 7.5 | 2.2 | 273 | 2 | 333 | 7.6 | 15 | 270 | 13 | 336 | 7.7 | 18 | 266 | 16 |  |  |  | 16.6667 | 85.3333
Wednesday | 2010-07-06 | 9:30:am | 31 | 4.6 | 333 | 7.4 | 2.8 | 283 | 4 | 336 | 7.6 | 22 | 278 | 17 | 339 | 7.7 | 28 | 271 | 25 | _ | 56 | 13000 | 21.4286 | 87.2727
|  | 11:30:am | 33 | 4.3 | 336 | 7.5 | 2.4 | 277 | 2 | 339 | 7.7 | 20 | 272 | 12 | 342 | 7.8 | 25 | 264 | 22 |  |  |  | 20 | 88
|  | 1:30:pm | 37 | 4 | 339 | 7.6 | 2 | 270 | 1 | 342 | 7.8 | 18 | 266 | 10 | 346 | 7.9 | 23 | 259 | 20 |  |  |  | 21.7391 | 88.8889
Thursday | 2010-07-07 | 9:30:am | 30 | 4.7 | 318 | 7.5 | 3.5 | 278 | 5 | 321 | 7.7 | 25 | 275 | 21 | 325 | 7.8 | 30 | 270 | 28 | _ | 59 | 13000 | 16.6667 | 86
|  | 11:30:am | 33 | 4.5 | 324 | 7.6 | 3 | 268 | 4 | 326 | 7.8 | 22 | 266 | 18 | 329 | 7.9 | 27 | 260 | 26 |  |  |  | 18.5185 | 86.3636
|  | 1:30:pm | 36 | 4.2 | 328 | 7.7 | 2.7 | 263 | 3 | 330 | 7.8 | 20 | 260 | 14 | 334 | 8 | 25 | 255 | 23 |  |  |  | 20 | 86.5
Friday | 2010-07-08 | 9:30:am | 33 | 4.3 | 326 | 7.4 | 2.9 | 298 | 7 | 328 | 7.6 | 24 | 294 | 19 | 331 | 7.7 | 29 | 288 | 27 | _ | 58 | 12500 | 17.2414 | 87.9167
|  | 11:30:am | 36 | 4 | 330 | 7.5 | 2.6 | 303 | 4 | 332 | 7.7 | 22 | 300 | 17 | 335 | 7.8 | 26 | 296 | 25 |  |  |  | 15.3846 | 88.1818
|  | 1:30:pm | 38 | 4 | 333 | 7.6 | 2 | 300 | 2 | 335 | 7.8 | 19 | 297 | 13 | 338 | 7.9 | 24 | 290 | 22 |  |  |  | 20.8333 | 89.4737
Saturday | 2010-07-09 | 9:30:am | 30 | 4.6 | 338 | 7.3 | 3.4 | 295 | 8 | 341 | 7.5 | 23 | 290 | 18 | 345 | 7.6 | 29 | 285 | 25 | _ | 57 | 12500 | 20.6897 | 85.2174
|  | 11:30:am | 33 | 4.4 | 342 | 7.4 | 3 | 287 | 6 | 344 | 7.6 | 25 | 284 | 15 | 349 | 7.7 | 33 | 280 | 28 |  |  |  | 24.2424 | 88
|  | 1:30:pm | 37 | 4.2 | 345 | 7.5 | 2.6 | 280 | 5 | 346 | 7.7 | 27 | 280 | 12 | 352 | 7.8 | 36 | 275 | 32 |  |  |  | 25 | 90.3704
Sunday | 2010-07-10 | 9:30:am | 31 | 4.5 | 326 | 7.4 | 3.1 | 322 | 6 | 329 | 7.5 | 26 | 311 | 16 | 334 | 7.6 | 29 | 306 | 27 | _ | 59 | 12500 | 10.3448 | 88.0769
|  | 11:30:am | 34 | 4.3 | 328 | 7.5 | 2.6 | 316 | 4 | 333 | 7.6 | 28 | 307 | 12 | 338 | 7.7 | 34 | 300 | 30 |  |  |  | 17.6471 | 90.7143
|  | 1:30:pm | 39 | 4 | 333 | 7.6 | 2.2 | 311 | 2 | 338 | 7.7 | 29 | 300 | 11 | 342 | 7.8 | 36 | 292 | 33 |  |  |  | 19.4444 | 92.4138
Monday | 2010-07-11 | 9:30:am | 33 | 4.8 | 331 | 7.3 | 2.8 | 314 | 9 | 334 | 7.5 | 24 | 300 | 21 | 337 | 7.6 | 27 | 294 | 23 | _ | 57 | 13000 | 11.1111 | 88.3333
|  | 11:30:am | 36 | 4.5 | 335 | 7.4 | 2.6 | 300 | 7 | 337 | 7.6 | 22 | 291 | 19 | 340 | 7.7 | 25 | 288 | 22 |  |  |  | 12 | 88.1818
|  | 1:30:pm | 38 | 4.2 | 338 | 7.5 | 2.3 | 294 | 6 | 341 | 7.7 | 20 | 286 | 16 | 343 | 7.8 | 24 | 280 | 20 |  |  |  | 16.6667 | 88.5
Tuesday | 2010-07-12 | 9:30:am | 31 | 4.6 | 321 | 7.4 | 2.5 | 278 | 8 | 329 | 7.6 | 25 | 275 | 22 | 334 | 7.7 | 28 | 270 | 26 | _ | 58 | 12500 | 10.7143 | 90
|  | 11:30:am | 33 | 4.2 | 324 | 7.5 | 2 | 266 | 6 | 327 | 7.7 | 22 | 262 | 18 | 331 | 7.8 | 25 | 258 | 22 |  |  |  | 12 | 90.9091
|  | 1:30:pm | 35 | 4 | 327 | 7.6 | 1.8 | 260 | 4 | 321 | 7.8 | 18 | 257 | 16 | 327 | 7.9 | 23 | 255 | 20 |  |  |  | 21.7391 | 90
Wednesday | 2010-07-13 | 9:30:am | 30 | 4.2 | 320 | 7.2 | 3.9 | 300 | 10 | 322 | 7.4 | 27 | 290 | 23 | 325 | 7.5 | 34 | 285 | 31 | _ | 55 | 13000 | 20.5882 | 85.5556
|  | 11:30:am | 32 | 4 | 323 | 7.3 | 3.4 | 314 | 8 | 326 | 7.5 | 26 | 300 | 20 | 328 | 7.6 | 31 | 290 | 28 |  |  |  | 16.129 | 86.9231
|  | 1:30:pm | 35 | 4 | 326 | 7.4 | 3 | 318 | 6 | 329 | 7.6 | 23 | 308 | 17 | 334 | 7.7 | 28 | 295 | 24 |  |  |  | 17.8571 | 86.9565
Thursday | 2010-07-14 | 9:30:am | 29 | 4.7 | 330 | 7.4 | 4 | 276 | 8 | 332 | 7.6 | 25 | 272 | 19 | 336 | 7.7 | 29 | 268 | 27 | _ | 58 | 13000 | 13.7931 | 84
|  | 11:30:am | 31 | 4.4 | 333 | 7.5 | 3.6 | 280 | 5 | 336 | 7.7 | 22 | 277 | 17 | 339 | 7.8 | 26 | 273 | 23 |  |  |  | 15.3846 | 83.6364
|  | 1:30:pm | 33 | 4.2 | 335 | 7.6 | 3.2 | 281 | 3 | 339 | 7.7 | 18 | 279 | 15 | 343 | 7.9 | 24 | 276 | 20 |  |  |  | 25 | 82.2222
Friday | 2010-07-15 | 9:30:am | 28 | 4.3 | 333 | 7.3 | 3.3 | 342 | 12 | 336 | 7.4 | 28 | 346 | 27 | 339 | 7.5 | 34 | 341 | 31 | 600 | 56 | 12500 | 17.6471 | 88.2143
|  | 11:30:am | 30 | 4 | 338 | 7.4 | 3 | 346 | 8 | 341 | 7.5 | 25 | 349 | 23 | 343 | 7.6 | 30 | 345 | 27 |  |  |  | 16.6667 | 88
|  | 1:30:pm | 32 | 4 | 342 | 7.5 | 2.7 | 349 | 7 | 346 | 7.6 | 23 | 353 | 21 | 348 | 7.7 | 33 | 348 | 29 |  |  |  | 30.303 | 88.2609
Saturday | 2010-07-16 | 9:30:am | 27 | 4.8 | 336 | 7.4 | 2.9 | 345 | 11 | 340 | 7.6 | 33 | 347 | 29 | 343 | 7.7 | 42 | 344 | 38 | 750 | 58 | 13000 | 21.4286 | 91.2121
|  | 11:30:am | 30 | 4.5 | 339 | 7.5 | 2.5 | 349 | 9 | 345 | 7.7 | 28 | 351 | 27 | 348 | 7.8 | 39 | 348 | 33 |  |  |  | 28.2051 | 91.0714
|  | 1:30:pm | 34 | 4.2 | 343 | 7.6 | 2 | 353 | 8 | 348 | 7.8 | 25 | 355 | 25 | 353 | 7.9 | 35 | 351 | 30 |  |  |  | 28.5714 | 92
Sunday | 2010-07-17 | 9:30:am | 29 | 4.6 | 330 | 7.2 | 3.9 | 340 | 13 | 335 | 7.4 | 36 | 345 | 31 | 340 | 7.5 | 45 | 341 | 34 | 750 | 59 | 12500 | 20 | 89.1667
|  | 11:30:am | 32 | 4.2 | 335 | 7.3 | 3.3 | 346 | 11 | 339 | 7.5 | 33 | 347 | 27 | 342 | 7.6 | 40 | 345 | 33 |  |  |  | 17.5 | 90
|  | 1:30:pm | 35 | 4 | 339 | 7.4 | 3 | 348 | 8 | 346 | 7.6 | 30 | 350 | 23 | 348 | 7.7 | 38 | 347 | 28 |  |  |  | 21.0526 | 90
Monday | 2010-07-18 | 9:30:am | 27 | 4.4 | 328 | 7.3 | 3.9 | 299 | 9 | 332 | 7.5 | 32 | 295 | 30 | 336 | 7.6 | 35 | 290 | 32 | _ | 57 | 13000 | 8.5714 | 87.8125
|  | 11:30:am | 29 | 4.2 | 331 | 7.4 | 3.6 | 289 | 7 | 336 | 7.6 | 28 | 286 | 24 | 339 | 7.7 | 33 | 282 | 30 |  |  |  | 15.1515 | 87.1429
|  | 1:30:pm | 32 | 4 | 336 | 7.5 | 3.3 | 277 | 5 | 341 | 7.7 | 25 | 273 | 20 | 345 | 7.8 | 30 | 270 | 26 |  |  |  | 16.6667 | 86.8
Tuesday | 2010-07-19 | 9:30:am | 28 | 4.3 | 333 | 7.4 | 4 | 267 | 8 | 337 | 7.6 | 27 | 263 | 25 | 342 | 7.7 | 35 | 260 | 30 | _ | 58 | 13000 | 22.8571 | 85.1852
|  | 11:30:am | 31 | 4 | 338 | 7.5 | 3.6 | 263 | 5 | 341 | 7.7 | 25 | 258 | 20 | 346 | 7.8 | 32 | 255 | 28 |  |  |  | 21.875 | 85.6
|  | 1:30:pm | 35 | 4 | 339 | 7.6 | 3.4 | 255 | 3 | 344 | 7.8 | 21 | 252 | 18 | 348 | 7.9 | 28 | 247 | 23 |  |  |  | 25 | 83.8095
Wednesday | 2010-07-20 | 9:30:am | 31 | 4.5 | 329 | 7.4 | 3.3 | 223 | 6 | 334 | 7.5 | 22 | 226 | 21 | 337 | 7.6 | 30 | 223 | 25 | _ | 59 | 13000 | 26.6667 | 85
|  | 11:30:am | 33 | 4.2 | 332 | 7.5 | 2.8 | 218 | 3 | 337 | 7.6 | 18 | 222 | 18 | 341 | 7.7 | 27 | 218 | 21 |  |  |  | 33.3333 | 84.4444
|  | 1:30:pm | 37 | 4 | 338 | 7.6 | 2.4 | 211 | 2 | 341 | 7.7 | 15 | 210 | 14 | 344 | 7.8 | 25 | 207 | 18 |  |  |  | 40 | 84
Thursday | 2010-07-21 | 9:30:am | 26 | 4.7 | 333 | 7.3 | 4.7 | 220 | 8 | 337 | 7.4 | 26 | 216 | 23 | 342 | 7.5 | 33 | 211 | 23 | _ | 57 | 13000 | 21.2121 | 81.9231
|  | 11:30:am | 28 | 4.4 | 339 | 7.4 | 3.8 | 213 | 5 | 342 | 7.5 | 22 | 211 | 19 | 346 | 7.6 | 29 | 207 | 20 |  |  |  | 24.1379 | 82.7273
|  | 1:30:pm | 32 | 4.2 | 345 | 7.5 | 3.5 | 208 | 2 | 348 | 7.6 | 19 | 206 | 15 | 351 | 7.7 | 26 | 201 | 16 |  |  |  | 26.9231 | 81.5789
Friday | 2010-07-22 | 9:30:am | 28 | 4.6 | 321 | 7.4 | 3.3 | 278 | 9 | 324 | 7.5 | 23 | 274 | 21 | 329 | 7.6 | 29 | 270 | 23 | _ | 50 | 10000 | 20.6897 | 85.6522
|  | 11:30:am | 30 | 4.3 | 318 | 7.5 | 2.9 | 274 | 7 | 321 | 7.6 | 21 | 270 | 18 | 327 | 7.7 | 27 | 266 | 19 |  |  |  | 22.2222 | 86.1905
|  | 1:30:pm | 31 | 4.1 | 315 | 7.6 | 2.4 | 269 | 5 | 317 | 7.7 | 18 | 266 | 15 | 321 | 7.8 | 25 | 261 | 15 |  |  |  | 28 | 86.6667
Saturday | 2010-07-23 | 9:30:am | 27 | 4.5 | 326 | 7.3 | 2.7 | 275 | 7 | 328 | 7.4 | 27 | 271 | 19 | 325 | 7.5 | 34 | 264 | 30 | _ | 59 | 13000 | 20.5882 | 90
|  | 11:30:am | 29 | 4.2 | 321 | 7.4 | 2.4 | 271 | 5 | 324 | 7.5 | 22 | 268 | 16 | 322 | 7.6 | 30 | 261 | 27 |  |  |  | 26.6667 | 89.0909
|  | 1:30:pm | 32 | 4 | 319 | 7.5 | 2 | 267 | 4 | 320 | 7.6 | 20 | 263 | 12 | 317 | 7.7 | 27 | 259 | 23 |  |  |  | 25.9259 | 90
Sunday | 2010-07-24 | 9:30:am | 29 | 4.4 | 333 | 7.3 | 3.6 | 288 | 8 | 337 | 7.4 | 29 | 284 | 19 | 341 | 7.5 | 34 | 280 | 28 | _ | 57 | 13000 | 14.7059 | 87.5862
|  | 11:30:am | 31 | 4.2 | 329 | 7.4 | 3.3 | 294 | 6 | 333 | 7.5 | 25 | 288 | 18 | 337 | 7.6 | 31 | 285 | 23 |  |  |  | 19.3548 | 86.8
|  | 1:30:pm | 33 | 4 | 325 | 7.5 | 3 | 299 | 5 | 327 | 7.6 | 23 | 294 | 16 | 333 | 7.7 | 29 | 290 | 20 |  |  |  | 20.6897 | 86.9565
Monday | 2010-07-25 | 9:30:am | 26 | 4.3 | 337 | 7.5 | 4.4 | 324 | 13 | 341 | 7.7 | 33 | 320 | 28 | 345 | 7.9 | 42 | 317 | 29 | 750 | 55 | 12500 | 21.4286 | 86.6667
|  | 11:30:am | 28 | 4 | 341 | 7.6 | 4 | 329 | 11 | 346 | 7.8 | 29 | 324 | 24 | 349 | 8 | 40 | 321 | 25 |  |  |  | 27.5 | 86.2069
|  | 1:30:pm | 30 | 4 | 344 | 7.7 | 3.7 | 334 | 9 | 348 | 7.8 | 25 | 327 | 21 | 353 | 8 | 37 | 326 | 21 |  |  |  | 32.4324 | 85.2
Tuesday | 2010-07-26 | 9:30:am | 28 | 4 | 331 | 7.2 | 4.7 | 338 | 15 | 337 | 7.4 | 36 | 333 | 32 | 339 | 7.6 | 45 | 330 | 33 | 900 | 59 | 12500 | 20 | 86.9444
|  | 11:30:am | 31 | 4 | 334 | 7.3 | 4.2 | 341 | 12 | 339 | 7.5 | 31 | 337 | 27 | 342 | 7.7 | 42 | 333 | 29 |  |  |  | 26.1905 | 86.4516
|  | 1:30:pm | 33 | 4 | 337 | 7.4 | 3.9 | 345 | 8 | 343 | 7.6 | 28 | 340 | 25 | 347 | 7.8 | 40 | 337 | 26 |  |  |  | 30 | 86.0714
Wednesday | 2010-07-27 | 9:30:am | 27 | 4.5 | 339 | 7.3 | 4 | 342 | 11 | 342 | 7.5 | 33 | 339 | 29 | 347 | 7.7 | 40 | 336 | 38 | 450 | 58 | 13000 | 17.5 | 87.8788
|  | 11:30:am | 29 | 4.2 | 343 | 7.4 | 3.7 | 347 | 8 | 347 | 7.6 | 28 | 342 | 26 | 351 | 7.8 | 36 | 340 | 33 |  |  |  | 22.2222 | 86.7857
|  | 1:30:pm | 31 | 4 | 346 | 7.5 | 3.3 | 351 | 7 | 350 | 7.7 | 24 | 347 | 23 | 353 | 7.9 | 33 | 342 | 30 |  |  |  | 27.2727 | 86.25
Thursday | 2010-07-28 | 9:30:am | 28 | 4.4 | 339 | 7.3 | 3.5 | 344 | 12 | 342 | 7.4 | 31 | 340 | 27 | 345 | 7.6 | 44 | 338 | 38 | 900 | 59 | 12500 | 29.5455 | 88.7097
|  | 11:30:am | 29 | 4.2 | 343 | 7.4 | 3 | 349 | 10 | 347 | 7.5 | 28 | 345 | 23 | 350 | 7.7 | 40 | 342 | 35 |  |  |  | 30 | 89.2857
|  | 1:30:pm | 31 | 4 | 348 | 7.5 | 2.9 | 353 | 8 | 353 | 7.6 | 25 | 347 | 20 | 355 | 7.8 | 38 | 344 | 32 |  |  |  | 34.2105 | 88.4
Friday | 2010-07-29 | 9:30:am | 27 | 4.6 | 341 | 7.4 | 4.4 | 340 | 10 | 346 | 7.5 | 33 | 337 | 29 | 349 | 7.7 | 47 | 333 | 40 | 900 | 57 | 12500 | 29.7872 | 86.6667
|  | 11:30:am | 29 | 4.3 | 346 | 7.5 | 4 | 345 | 8 | 349 | 7.6 | 26 | 341 | 26 | 353 | 7.8 | 46 | 337 | 37 |  |  |  | 43.4783 | 84.6154
|  | 1:30:pm | 32 | 4 | 348 | 7.6 | 3.6 | 348 | 7 | 353 | 7.7 | 23 | 344 | 22 | 356 | 7.9 | 40 | 341 | 35 |  |  |  | 42.5 | 84.3478
Saturday | 2010-07-30 | 9:30:am | 29 | 4.5 | 339 | 7.4 | 4 | 339 | 12 | 343 | 7.6 | 29 | 336 | 25 | 346 | 7.8 | 39 | 331 | 35 | 750 | 60 | 12500 | 25.641 | 86.2069
|  | 11:30:am | 32 | 4.2 | 343 | 7.5 | 3.8 | 343 | 9 | 348 | 7.7 | 26 | 340 | 22 | 349 | 7.9 | 36 | 335 | 33 |  |  |  | 27.7778 | 85.3846
|  | 1:30:pm | 34 | 4 | 346 | 7.6 | 3.5 | 348 | 7 | 354 | 7.8 | 22 | 344 | 20 | 357 | 8 | 33 | 340 | 28 |  |  |  | 33.3333 | 84.0909
Sunday | 2010-07-31 | 9:30 | 26 | 4.8 | 347 | 7.3 | 3.8 | 345 | 14 | 350 | 7.5 | 34 | 340 | 29 | 353 | 7.7 | 42 | 331 | 39 | 900 | 59 | 12500 | 19.0476 | 88.8235
|  | 11:30 | 28 | 4.6 | 350 | 7.4 | 3.5 | 350 | 12 | 354 | 7.6 | 30 | 346 | 27 | 359 | 7.8 | 40 | 340 | 32 |  |  |  | 25 | 88.3333
|  | 1:30:pm | 31 | 4.3 | 353 | 7.5 | 3.2 | 353 | 10 | 357 | 7.7 | 24 | 350 | 25 | 363 | 7.9 | 38 | 346 | 27 |  |  |  | 36.8421 | 86.6667

## 8
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-08-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr)
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | S-R | S-SUP
Sunday | 2010-08-01 | 9:30:am | 26 | 4.2 | 333 | 7.4 | 4.2 | 321 | 9 | 336 | 7.5 | 29 | 318 | 23 | 339 | 7.7 | 36 | 314 | 29 | _ | 54 | 12500 | 19.4444 | 85.5172
|  | 11:30:am | 28 | 4 | 330 | 7.5 | 4 | 318 | 7 | 333 | 7.6 | 25 | 314 | 20 | 335 | 7.8 | 33 | 310 | 25 |  |  |  | 24.2424 | 84
|  | 1:30:pm | 31 | 4 | 327 | 7.6 | 3.6 | 311 | 6 | 330 | 7.7 | 23 | 307 | 18 | 332 | 7.9 | 29 | 303 | 22 |  |  |  | 20.6897 | 84.3478
Monday | 2010-08-02 | 9:30:am | 28 | 4.4 | 321 | 7.5 | 4 | 306 | 7 | 326 | 7.6 | 27 | 301 | 19 | 330 | 7.7 | 34 | 296 | 31 | _ | 58 | 13000 | 20.5882 | 85.1852
|  | 11:30:am | 31 | 4.2 | 318 | 7.6 | 3.5 | 297 | 5 | 322 | 7.7 | 23 | 292 | 17 | 325 | 7.8 | 29 | 289 | 28 |  |  |  | 20.6897 | 84.7826
|  | 1:30:pm | 34 | 4 | 309 | 7.7 | 3.2 | 291 | 4 | 317 | 7.8 | 20 | 286 | 14 | 321 | 7.9 | 26 | 282 | 25 |  |  |  | 23.0769 | 84
Tuesday | 2010-08-03 | 9:30:am | 29 | 4.3 | 339 | 7.4 | 4.8 | 333 | 13 | 343 | 7.6 | 30 | 330 | 29 | 347 | 7.8 | 54 | 327 | 43 | 600 | 59 | 13000 | 44.4444 | 84
|  | 11:30:am | 32 | 4 | 344 | 7.5 | 4.4 | 339 | 11 | 348 | 7.7 | 26 | 333 | 25 | 354 | 7.9 | 48 | 330 | 37 |  |  |  | 45.8333 | 83.0769
|  | 1:30:pm | 34 | 4 | 349 | 7.6 | 3.9 | 343 | 9 | 353 | 7.8 | 23 | 337 | 22 | 359 | 8 | 46 | 333 | 33 |  |  |  | 50 | 83.0435
Wednesday | 2010-08-04 | 9:30:am | 27 | 4.6 | 345 | 7.5 | 4.9 | 349 | 15 | 349 | 7.7 | 45 | 344 | 36 | 354 | 7.9 | 57 | 340 | 45 | 900 | 56 | 12500 | 21.0526 | 89.1111
|  | 11:30:am | 29 | 4.3 | 341 | 7.6 | 4.5 | 353 | 12 | 345 | 7.8 | 40 | 349 | 33 | 350 | 8 | 55 | 345 | 40 |  |  |  | 27.2727 | 88.75
|  | 1:30:pm | 32 | 4 | 338 | 7.7 | 4 | 359 | 10 | 342 | 7.8 | 35 | 353 | 30 | 345 | 8 | 53 | 349 | 38 |  |  |  | 33.9623 | 88.5714
Thursday | 2010-08-05 | 9:30:am | 26 | 4.2 | 339 | 7.3 | 4.7 | 353 | 18 | 343 | 7.5 | 47 | 350 | 38 | 348 | 7.7 | 78 | 347 | 67 | 1500 | 58 | 13000 | 39.7436 | 90
|  | 11:30:am | 29 | 4 | 343 | 7.4 | 4.3 | 359 | 15 | 347 | 7.6 | 41 | 355 | 35 | 351 | 7.8 | 82 | 350 | 59 |  |  |  | 50 | 89.5122
|  | 1:30:pm | 31 | 4 | 347 | 7.5 | 4 | 367 | 12 | 354 | 7.7 | 36 | 362 | 33 | 358 | 7.9 | 85 | 355 | 55 |  |  |  | 57.6471 | 88.8889
Friday | 2010-08-06 | 9:30:am | 28 | 4.3 | 345 | 7.2 | 4.8 | 351 | 16 | 348 | 7.4 | 36 | 348 | 32 | 354 | 7.6 | 48 | 344 | 44 | 1500 | 56 | 13000 | 25 | 86.6667
|  | 11:30:am | 31 | 4 | 348 | 7.3 | 4.3 | 355 | 13 | 351 | 7.5 | 33 | 352 | 28 | 358 | 7.7 | 44 | 347 | 40 |  |  |  | 25 | 86.9697
|  | 1:30:pm | 33 | 4 | 352 | 7.4 | 4 | 358 | 11 | 355 | 7.6 | 30 | 355 | 25 | 361 | 7.8 | 40 | 352 | 36 |  |  |  | 25 | 86.6667
Saturday | 2010-08-07 | 9:30:am | 26 | 4.5 | 344 | 7.3 | 4.2 | 356 | 15 | 348 | 7.5 | 39 | 353 | 38 | 353 | 7.7 | 49 | 348 | 43 | 1500 | 59 | 13000 | 20.4082 | 89.2308
|  | 11:30:am | 28 | 4.2 | 342 | 7.4 | 3.8 | 361 | 11 | 346 | 7.6 | 35 | 356 | 35 | 350 | 7.8 | 44 | 353 | 40 |  |  |  | 20.4545 | 89.1429
|  | 1:30:pm | 31 | 4 | 339 | 7.5 | 3.5 | 367 | 9 | 342 | 7.7 | 31 | 362 | 32 | 347 | 7.9 | 42 | 358 | 39 |  |  |  | 26.1905 | 88.7097
Sunday | 2010-08-08 | 9:30:am | 25 | 4.4 | 333 | 7.4 | 4 | 355 | 14 | 338 | 7.6 | 39 | 351 | 33 | 345 | 7.8 | 44 | 346 | 39 | 900 | 58 | 12500 | 11.3636 | 89.7436
|  | 11:30:am | 27 | 4.2 | 335 | 7.5 | 4 | 362 | 11 | 339 | 7.7 | 33 | 357 | 28 | 347 | 7.9 | 40 | 349 | 35 |  |  |  | 17.5 | 87.8788
|  | 1:30:pm | 30 | 4 | 339 | 7.6 | 4 | 369 | 8 | 344 | 7.8 | 29 | 359 | 26 | 349 | 8 | 37 | 354 | 33 |  |  |  | 21.6216 | 86.2069
Monday | 2010-08-09 | 9:30:am | 27 | 4.4 | 339 | 7.3 | 4 | 341 | 13 | 342 | 7.5 | 39 | 340 | 31 | 347 | 7.7 | 46 | 337 | 41 | 900 | 57 | 12500 | 15.2174 | 89.7436
|  | 11:30:am | 29 | 4.2 | 343 | 7.4 | 3.5 | 346 | 11 | 347 | 7.6 | 35 | 343 | 28 | 353 | 7.8 | 42 | 341 | 38 |  |  |  | 16.6667 | 90
|  | 1:30:pm | 32 | 4 | 346 | 7.5 | 3.2 | 349 | 8 | 353 | 7.7 | 31 | 347 | 24 | 359 | 7.9 | 40 | 345 | 35 |  |  |  | 22.5 | 89.6774
Tuesday | 2010-08-10 | 9:30:am | 33 | 4.5 | 339 | 7.2 | 4.5 | 345 | 13 | 343 | 7.3 | 36 | 342 | 31 | 346 | 7.5 | 44 | 338 | 39 | 900 | 59 | 12500 | 18.1818 | 87.5
|  | 11:30:am | 36 | 4.2 | 335 | 7.3 | 4.2 | 348 | 11 | 338 | 7.4 | 33 | 346 | 28 | 342 | 7.6 | 40 | 342 | 35 |  |  |  | 17.5 | 87.2727
|  | 1:30:pm | 40 | 4 | 330 | 7.2 | 4 | 351 | 9 | 333 | 7.5 | 30 | 349 | 25 | 336 | 7.7 | 37 | 346 | 33 |  |  |  | 18.9189 | 86.6667
Wednesday | 2010-08-11 | 9:30:am | 30 | 4.3 | 345 | 7.1 | 4 | 349 | 12 | 349 | 7.3 | 100 | 344 | 99 | 357 | 7.7 | 650 | 340 | 157 | 4500 | 57 | 13000 | 84.6154 | 96
|  | 11:30:am | 34 | 4 | 340 | 7.2 | 3.7 | 353 | 9 | 344 | 7.4 | 88 | 348 | 87 | 363 | 7.8 | 534 | 343 | 143 |  |  |  | 83.5206 | 95.7955
|  | 1:30:pm | 38 | 4 | 336 | 7.3 | 3.3 | 356 | 7 | 340 | 7.5 | 75 | 353 | 77 | 366 | 7.9 | 423 | 348 | 134 |  |  |  | 82.2695 | 95.6
Thursday | 2010-08-12 | 9:30:am | 34 | 4.4 | 348 | 7.3 | 3.7 | 342 | 14 | 353 | 7.5 | 27 | 338 | 22 | 358 | 7.7 | 48 | 333 | 44 | 1200 | 58 | 12500 | 43.75 | 86.2963
|  | 11:30:am | 37 | 4.2 | 343 | 7.4 | 3.4 | 347 | 11 | 350 | 7.6 | 22 | 342 | 20 | 360 | 7.8 | 44 | 340 | 39 |  |  |  | 50 | 84.5455
|  | 1:30:pm | 42 | 4 | 340 | 7.5 | 3 | 349 | 10 | 345 | 7.7 | 18 | 346 | 16 | 366 | 7.9 | 40 | 343 | 34 |  |  |  | 55 | 83.3333
Friday | 2010-08-13 | 9:30:am | 29 | 4.5 | 349 | 7.4 | 3.9 | 347 | 14 | 353 | 7.6 | 33 | 345 | 36 | 357 | 7.8 | 44 | 342 | 39 | 1200 | 55 | 13000 | 25 | 88.1818
|  | 11:30:am | 32 | 4.2 | 351 | 7.5 | 3.4 | 351 | 11 | 356 | 7.7 | 28 | 348 | 34 | 362 | 7.9 | 40 | 345 | 36 |  |  |  | 30 | 87.8571
|  | 1:30:pm | 35 | 4 | 357 | 7.6 | 3 | 357 | 9 | 362 | 7.8 | 26 | 353 | 29 | 367 | 8 | 37 | 349 | 33 |  |  |  | 29.7297 | 88.4615
Saturday | 2010-08-14 | 9:30:am | 30 | 4.8 | 344 | 7.3 | 4.3 | 353 | 12 | 348 | 7.5 | 38 | 350 | 34 | 352 | 7.7 | 44 | 346 | 37 | 1200 | 58 | 13000 | 13.6364 | 88.6842
|  | 11:30:am | 33 | 4.5 | 347 | 7.4 | 4 | 356 | 9 | 353 | 7.6 | 33 | 353 | 30 | 357 | 7.8 | 39 | 349 | 33 |  |  |  | 15.3846 | 87.8788
|  | 1:30:pm | 37 | 4.2 | 350 | 7.5 | 3.8 | 359 | 6 | 358 | 7.7 | 29 | 357 | 27 | 362 | 7.9 | 35 | 353 | 30 |  |  |  | 17.1429 | 86.8966
Sunday | 2010-08-15 | 9:30:am | 27 | 4.4 | 348 | 7.2 | 3.7 | 346 | 14 | 352 | 7.5 | 39 | 342 | 33 | 356 | 7.8 | 47 | 338 | 42 | 1200 | 56 | 12500 | 17.0213 | 90.5128
|  | 11:30:am | 30 | 4.2 | 352 | 7.3 | 3.3 | 349 | 10 | 358 | 7.6 | 42 | 347 | 37 | 360 | 7.9 | 44 | 342 | 38 |  |  |  | 4.5455 | 92.1429
|  | 1:30:pm | 32 | 4 | 358 | 7.4 | 2.9 | 353 | 7 | 362 | 7.7 | 44 | 351 | 40 | 364 | 7.9 | 49 | 346 | 44 |  |  |  | 10.2041 | 93.4091
Monday | 2010-08-16 | 9:30:am | 29 | 4.6 | 352 | 7.3 | 4.3 | 349 | 12 | 356 | 7.6 | 46 | 345 | 42 | 358 | 7.7 | 57 | 342 | 46 | 1250 | 58 | 13000 | 19.2982 | 90.6522
|  | 11:30:am | 31 | 4.3 | 357 | 7.4 | 4 | 354 | 9 | 360 | 7.7 | 42 | 348 | 38 | 362 | 7.8 | 55 | 345 | 40 |  |  |  | 23.6364 | 90.4762
|  | 1:30:pm | 34 | 4 | 361 | 7.5 | 3.8 | 358 | 6 | 363 | 7.8 | 37 | 354 | 34 | 367 | 7.9 | 52 | 349 | 38 |  |  |  | 28.8462 | 89.7297
Tuesday | 2010-08-17 | 9:30:am | 32 | 4.8 | 349 | 7.3 | 3.2 | 350 | 14 | 353 | 7.5 | 36 | 348 | 31 | 356 | 7.7 | 53 | 343 | 43 | 1200 | 59 | 12500 | 32.0755 | 91.1111
|  | 11:30:am | 35 | 4.4 | 353 | 7.4 | 2.9 | 356 | 12 | 356 | 7.6 | 33 | 353 | 28 | 359 | 7.8 | 48 | 348 | 39 |  |  |  | 31.25 | 91.2121
|  | 1:30:pm | 38 | 4.2 | 358 | 7.5 | 2.7 | 359 | 10 | 363 | 7.7 | 30 | 356 | 25 | 366 | 7.8 | 44 | 353 | 35 |  |  |  | 31.8182 | 91
Wednesday | 2010-08-18 | 9:30:am | 28 | 4.2 | 345 | 7.4 | 3.6 | 344 | 10 | 349 | 7.6 | 31 | 341 | 26 | 352 | 7.8 | 43 | 338 | 37 | 1050 | 57 | 13000 | 27.907 | 88.3871
|  | 11:30:am | 31 | 4 | 348 | 7.5 | 3.2 | 348 | 8 | 354 | 7.7 | 27 | 345 | 23 | 357 | 7.9 | 39 | 343 | 33 |  |  |  | 30.7692 | 88.1481
|  | 1:30:pm | 33 | 4 | 351 | 7.6 | 3 | 353 | 5 | 357 | 7.8 | 25 | 348 | 20 | 360 | 8 | 36 | 346 | 30 |  |  |  | 30.5556 | 88
Thursday | 2010-08-19 | 9:30:am | 27 | 4.5 | 346 | 7.2 | 4.6 | 358 | 12 | 349 | 7.5 | 44 | 354 | 37 | 351 | 7.7 | 58 | 350 | 42 | 2100 | 58 | 13000 | 24.1379 | 89.5455
|  | 11:30:am | 29 | 4.2 | 352 | 7.3 | 3.9 | 360 | 8 | 356 | 7.6 | 40 | 357 | 33 | 357 | 7.8 | 55 | 355 | 38 |  |  |  | 27.2727 | 90.25
|  | 1:30:pm | 32 | 4 | 357 | 7.4 | 3.3 | 366 | 4 | 362 | 7.7 | 37 | 362 | 30 | 363 | 7.9 | 53 | 357 | 35 |  |  |  | 30.1887 | 91.0811
Friday | 2010-08-20 | 9:30:am | 27 | 4.6 | 349 | 7.3 | 3.8 | 363 | 13 | 354 | 7.6 | 42 | 360 | 33 | 358 | 7.8 | 72 | 358 | 49 | 2100 | 59 | 13000 | 41.6667 | 90.9524
|  | 11:30:am | 30 | 4.3 | 354 | 7.4 | 3.3 | 367 | 11 | 359 | 7.7 | 37 | 363 | 31 | 362 | 7.9 | 68 | 361 | 45 |  |  |  | 45.5882 | 91.0811
|  | 1:30:pm | 33 | 4 | 358 | 7.5 | 2.9 | 369 | 8 | 364 | 7.8 | 34 | 366 | 28 | 367 | 8 | 66 | 363 | 43 |  |  |  | 48.4848 | 91.4706
Saturday | 2010-08-21 | 9:30:am | 29 | 4.6 | 354 | 7.2 | 4.6 | 354 | 12 | 358 | 7.4 | 48 | 350 | 33 | 355 | 7.6 | 59 | 345 | 45 | 1500 | 57 | 13000 | 18.6441 | 90.4167
|  | 11:30:am | 32 | 4.2 | 359 | 7.3 | 4.3 | 358 | 10 | 363 | 7.5 | 44 | 355 | 28 | 359 | 7.7 | 63 | 349 | 40 |  |  |  | 30.1587 | 90.2273
|  | 1:30:pm | 37 | 4 | 362 | 7.4 | 4 | 361 | 8 | 367 | 7.6 | 48 | 359 | 24 | 363 | 7.8 | 68 | 354 | 36 |  |  |  | 29.4118 | 91.6667
Sunday | 2010-08-22 | 9:30:am | 27 | 4.3 | 359 | 7.3 | 4.8 | 348 | 14 | 363 | 7.5 | 40 | 344 | 38 | 360 | 7.7 | 48 | 340 | 41 | 1350 | 50 | 10000 | 16.6667 | 88
|  | 11:30:am | 29 | 4 | 363 | 7.4 | 4.4 | 352 | 12 | 367 | 7.6 | 36 | 348 | 33 | 362 | 7.8 | 44 | 344 | 38 |  |  |  | 18.1818 | 87.7778
|  | 1:30:pm | 32 | 4 | 366 | 7.5 | 3.8 | 356 | 10 | 370 | 7.7 | 33 | 352 | 29 | 367 | 7.9 | 42 | 347 | 33 |  |  |  | 21.4286 | 88.4848
Monday | 2010-08-23 | 9:30:am | 26 | 4.4 | 362 | 7.4 | 4.2 | 349 | 11 | 366 | 7.6 | 37 | 346 | 31 | 361 | 7.8 | 49 | 341 | 40 | 1200 | 59 | 13000 | 24.4898 | 88.6486
|  | 11:30:am | 28 | 4.2 | 366 | 7.5 | 4 | 355 | 9 | 369 | 7.7 | 33 | 349 | 28 | 366 | 7.9 | 45 | 346 | 35 |  |  |  | 26.6667 | 87.8788
|  | 1:30:pm | 31 | 4 | 368 | 7.6 | 3.6 | 360 | 8 | 372 | 7.8 | 30 | 354 | 25 | 370 | 8 | 43 | 350 | 31 |  |  |  | 30.2326 | 88
Tuesday | 2010-08-24 | 9:30:am | 29 | 4.5 | 359 | 7.3 | 3.8 | 345 | 13 | 363 | 7.5 | 31 | 341 | 26 | 360 | 7.7 | 48 | 338 | 38 | 1200 | 57 | 13000 | 35.4167 | 87.7419
|  | 11:30:am | 32 | 4.3 | 363 | 7.4 | 3.4 | 351 | 10 | 367 | 7.6 | 29 | 347 | 27 | 366 | 7.8 | 44 | 343 | 32 |  |  |  | 34.0909 | 88.2759
|  | 1:30:pm | 34 | 4 | 367 | 7.5 | 3 | 355 | 8 | 370 | 7.7 | 27 | 352 | 25 | 368 | 7.9 | 40 | 348 | 29 |  |  |  | 32.5 | 88.8889
Wednesday | 2010-08-25 | 9:30:am | 28 | 4.3 | 357 | 7.4 | 4.7 | 347 | 14 | 361 | 7.6 | 32 | 341 | 27 | 358 | 7.8 | 45 | 337 | 36 | 1200 | 55 | 12500 | 28.8889 | 85.3125
|  | 11:30:am | 30 | 4 | 360 | 7.5 | 4.2 | 352 | 11 | 366 | 7.7 | 28 | 348 | 25 | 363 | 7.9 | 43 | 343 | 33 |  |  |  | 34.8837 | 85
|  | 1:30:pm | 33 | 4 | 362 | 7.6 | 3.7 | 359 | 9 | 368 | 7.8 | 23 | 354 | 22 | 366 | 8 | 40 | 348 | 27 |  |  |  | 42.5 | 83.913
Thursday | 2010-08-26 | 9:30:am | 30 | 4.2 | 333 | 7.3 | 4.1 | 342 | 11 | 337 | 7.5 | 42 | 338 | 29 | 342 | 7.8 | 75 | 335 | 45 | 2100 | 59 | 12500 | 44 | 90.2381
|  | 11:30:am | 32 | 4 | 337 | 7.4 | 3.6 | 345 | 9 | 342 | 7.6 | 35 | 342 | 25 | 346 | 7.9 | 79 | 338 | 40 |  |  |  | 55.6962 | 89.7143
|  | 1:30:pm | 36 | 4 | 341 | 7.5 | 3.1 | 349 | 7 | 346 | 7.7 | 33 | 346 | 23 | 351 | 8 | 83 | 342 | 34 |  |  |  | 60.241 | 90.6061
Friday | 2010-08-27 | 9:30:am | 29 | 4.5 | 345 | 7.3 | 4.4 | 349 | 14 | 349 | 7.5 | 42 | 345 | 38 | 352 | 7.7 | 59 | 344 | 48 | 1750 | 58 | 13000 | 28.8136 | 89.5238
|  | 11:30:am | 32 | 4.2 | 349 | 7.4 | 4 | 353 | 11 | 353 | 7.6 | 38 | 347 | 34 | 357 | 7.8 | 63 | 346 | 55 |  |  |  | 39.6825 | 89.4737
|  | 1:30:pm | 34 | 4 | 352 | 7.5 | 3.7 | 358 | 10 | 358 | 7.7 | 35 | 353 | 31 | 361 | 7.9 | 76 | 348 | 61 |  |  |  | 53.9474 | 89.4286
Thursday | 2010-08-28 | 9:30:am | 31 | 4.7 | 352 | 7.4 | 3.9 | 351 | 12 | 356 | 7.6 | 40 | 348 | 35 | 360 | 7.8 | 65 | 345 | 55 | 1900 | 59 | 12500 | 38.4615 | 90.25
|  | 11:30:am | 34 | 4.3 | 357 | 7.5 | 3.4 | 354 | 10 | 361 | 7.7 | 36 | 352 | 31 | 365 | 7.9 | 68 | 349 | 62 |  |  |  | 47.0588 | 90.5556
|  | 1:30:pm | 38 | 4 | 360 | 7.6 | 2.9 | 357 | 8 | 366 | 7.8 | 30 | 356 | 28 | 368 | 8 | 77 | 353 | 68 |  |  |  | 61.039 | 90.3333
Friday | 2010-08-29 | 9:30:am | 28 | 4.2 | 350 | 7.5 | 2.9 | 355 | 10 | 355 | 7.7 | 38 | 350 | 33 | 358 | 7.8 | 72 | 347 | 62 | 2250 | 57 | 12500 | 47.2222 | 92.3684
|  | 11:30:am | 30 | 4 | 355 | 7.6 | 2.5 | 358 | 8 | 358 | 7.8 | 33 | 353 | 29 | 362 | 7.9 | 75 | 350 | 66 |  |  |  | 56 | 92.4242
|  | 1:30:pm | 33 | 4 | 358 | 7.7 | 2.2 | 363 | 7 | 363 | 7.8 | 28 | 358 | 25 | 367 | 7.9 | 70 | 355 | 68 |  |  |  | 60 | 92.1429
Saturday | 2010-08-30 | 9:30:am | 27 |  | 349 | 7.2 | 3.6 | 350 | 11 | 353 | 7.4 | 39 | 347 | 31 | 357 | 7.6 | 49 | 343 | 39 | 1350 | 60 | 12500 | 20.4082 | 90.7692
|  | 11:30:am | 29 | 4.2 | 353 | 7.3 | 3.3 | 353 | 8 | 357 | 7.5 | 36 | 350 | 28 | 362 | 7.7 | 52 | 348 | 36 |  |  |  | 30.7692 | 90.8333
|  | 1:30:pm | 31 | 4 | 356 | 7.4 | 3 | 358 | 6 | 361 | 7.6 | 31 | 355 | 25 | 367 | 7.8 | 55 | 353 | 33 |  |  |  | 43.6364 | 90.3226
Sunday | 2010-08-31 | 9:30 | 25 | 4.6 | 354 | 7.3 | 4.8 | 342 | 13 | 358 | 7.5 | 36 | 338 | 30 | 363 | 7.7 | 56 | 335 | 45 | 1650 | 59 | 12500 | 35.7143 | 86.6667
|  | 11:30 | 27 | 4.2 | 358 | 7.4 | 4.2 | 347 | 10 | 362 | 7.6 | 33 | 343 | 27 | 366 | 7.8 | 49 | 339 | 40 |  |  |  | 32.6531 | 87.2727
|  | 1:30:pm | 30 | 4 | 359 | 7.5 | 3.7 | 352 | 7 | 366 | 7.7 | 30 | 348 | 22 | 369 | 7.9 | 45 | 343 | 36 |  |  |  | 33.3333 | 87.6667

## 9
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-09-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr)
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | S-R | S-SUP
Wednesday | 2010-09-01 | 9:30:am | 26 | 4.3 | 342 | 7.3 | 3.8 | 349 | 11 | 347 | 7.5 | 24 | 345 | 29 | 350 | 7.7 | 59 | 342 | 39 | 1950 | 54 | 12500 | 59.322 | 84.1667
|  | 11:30:am | 28 | 4 | 346 | 7.4 | 3.4 | 353 | 9 | 349 | 7.6 | 22 | 349 | 25 | 354 | 7.8 | 55 | 345 | 35 |  |  |  | 60 | 84.5455
|  | 1:30:pm | 31 | 4 | 349 | 7.5 | 3 | 358 | 7 | 353 | 7.7 | 19 | 353 | 22 | 358 | 7.9 | 48 | 348 | 32 |  |  |  | 60.4167 | 84.2105
Thursday | 2010-09-02 | 9:30:am | 28 | 4.5 | 341 | 7.2 | 4.6 | 353 | 12 | 346 | 7.4 | 25 | 349 | 31 | 349 | 7.6 | 45 | 342 | 40 | 1350 | 58 | 13000 | 44.4444 | 81.6
|  | 11:30:am | 31 | 4.2 | 344 | 7.3 | 4 | 358 | 10 | 349 | 7.5 | 22 | 355 | 27 | 352 | 7.7 | 44 | 347 | 37 |  |  |  | 50 | 81.8182
|  | 1:30:pm | 33 | 4 | 347 | 7.4 | 3.6 | 360 | 8 | 353 | 7.6 | 20 | 358 | 23 | 358 | 7.8 | 47 | 352 | 34 |  |  |  | 57.4468 | 82
Friday | 2010-09-03 | 9:30:am | 27 | 4.6 | 349 | 7.4 | 3.2 | 350 | 14 | 352 | 7.7 | 29 | 344 | 27 | 355 | 7.9 | 47 | 341 | 37 | 1350 | 59 | 13000 | 38.2979 | 88.9655
|  | 11:30:am | 29 | 4.3 | 354 | 7.5 | 2.9 | 353 | 12 | 358 | 7.8 | 24 | 348 | 23 | 360 | 7.9 | 44 | 345 | 33 |  |  |  | 45.4545 | 87.9167
|  | 1:30:pm | 32 | 4 | 358 | 7.6 | 2.7 | 357 | 10 | 362 | 7.9 | 22 | 354 | 19 | 366 | 8 | 40 | 349 | 29 |  |  |  | 45 | 87.7273
Saturday | 2010-09-04 | 9:30:am | 25 | 4.5 | 346 | 7.3 | 3.8 | 356 | 16 | 349 | 7.5 | 31 | 352 | 33 | 352 | 7.7 | 55 | 348 | 42 | 1950 | 56 | 12500 | 43.6364 | 87.7419
|  | 11:30:am | 28 | 4.2 | 349 | 7.4 | 3.3 | 359 | 13 | 353 | 7.6 | 28 | 355 | 29 | 357 | 7.8 | 50 | 353 | 38 |  |  |  | 44 | 88.2143
|  | 1:30:pm | 31 | 4 | 353 | 7.5 | 2.8 | 362 | 11 | 357 | 7.7 | 25 | 359 | 25 | 362 | 7.9 | 48 | 356 | 33 |  |  |  | 47.9167 | 88.8
Sunday | 2010-09-05 | 9:30:am | 23 | 4.6 | 349 | 7.4 | 3.1 | 360 | 13 | 353 | 7.6 | 27 | 357 | 25 | 357 | 7.8 | 49 | 355 | 36 | 1350 | 58 | 13000 | 44.898 | 88.5185
|  | 11:30:am | 26 | 4.2 | 355 | 7.5 | 2.8 | 357 | 11 | 358 | 7.7 | 22 | 354 | 21 | 362 | 7.9 | 47 | 350 | 33 |  |  |  | 53.1915 | 87.2727
|  | 1:30:pm | 30 | 4 | 358 | 7.6 | 2.6 | 355 | 9 | 363 | 7.8 | 18 | 350 | 18 | 366 | 8 | 44 | 347 | 29 |  |  |  | 59.0909 | 85.5556
Monday | 2010-09-06 | 9:30:am | 27 | 4.2 | 349 | 7.3 | 3.4 | 348 | 10 | 354 | 7.5 | 20 | 343 | 27 | 358 | 7.6 | 53 | 340 | 39 | 1700 | 56 | 13000 | 62.2642 | 83
|  | 11:30:am | 30 | 4 | 352 | 7.4 | 3 | 349 | 8 | 359 | 7.6 | 18 | 345 | 23 | 362 | 7.7 | 50 | 342 | 41 |  |  |  | 64 | 83.3333
|  | 1:30:pm | 33 | 4 | 355 | 7.5 | 2.8 | 353 | 6 | 362 | 7.7 | 16 | 349 | 20 | 366 | 7.8 | 47 | 347 | 43 |  |  |  | 65.9574 | 82.5
Tuesday | 2010-09-07 | 9:30:am | 28 | 4.4 | 358 | 7.4 | 3.7 | 345 | 9 | 363 | 7.6 | 24 | 342 | 23 | 366 | 7.8 | 59 | 339 | 48 | 1950 | 59 | 13000 | 59.322 | 84.5833
|  | 11:30:am | 30 | 4.2 | 361 | 7.5 | 3.3 | 348 | 7 | 367 | 7.7 | 22 | 346 | 19 | 370 | 7.9 | 55 | 343 | 44 |  |  |  | 60 | 85
|  | 1:30:pm | 32 | 4 | 364 | 7.6 | 3 | 352 | 5 | 369 | 7.8 | 17 | 349 | 15 | 373 | 7.9 | 53 | 345 | 41 |  |  |  | 67.9245 | 82.3529
Wednesday | 2010-09-08 | 9:30:am | 27 | 4.3 | 342 | 7.3 | 3 | 348 | 9 | 345 | 7.5 | 36 | 344 | 30 | 348 | 7.7 | 48 | 341 | 40 | 1200 | 58 | 12500 | 25 | 91.6667
|  | 11:30:am | 29 | 4 | 346 | 7.4 | 2.8 | 353 | 7 | 349 | 7.6 | 33 | 348 | 27 | 353 | 7.8 | 51 | 344 | 35 |  |  |  | 35.2941 | 91.5152
|  | 1:30:pm | 31 | 4 | 349 | 7.5 | 2.5 | 356 | 6 | 353 | 7.7 | 29 | 353 | 23 | 357 | 7.9 | 53 | 349 | 33 |  |  |  | 45.283 | 91.3793
Thursday | 2010-09-09 | 9:30:am | 23 | 4.4 | 353 | 7.3 | 4 | 344 | 14 | 356 | 7.5 | 29 | 341 | 27 | 360 | 7.7 | 44 | 339 | 36 | 1200 | 57 | 12500 | 34.0909 | 86.2069
|  | 11:30:am | 25 | 4.2 | 357 | 7.4 | 3.6 | 340 | 11 | 360 | 7.6 | 25 | 339 | 24 | 363 | 7.8 | 41 | 336 | 33 |  |  |  | 39.0244 | 85.6
|  | 1:30:pm | 28 | 4 | 359 | 7.5 | 3.2 | 337 | 10 | 364 | 7.7 | 23 | 336 | 21 | 367 | 7.9 | 38 | 333 | 30 |  |  |  | 39.4737 | 86.087
Friday | 2010-09-10 | 9:30:am | 25 | 4.8 | 351 | 7.4 | 3.9 | 352 | 12 | 355 | 7.6 | 31 | 350 | 29 | 358 | 7.8 | 49 | 348 | 41 | 1200 | 59 | 12500 | 36.7347 | 87.4194
|  | 11:30:am | 26 | 4.4 | 353 | 7.5 | 3.3 | 348 | 10 | 359 | 7.7 | 28 | 346 | 25 | 361 | 7.9 | 45 | 345 | 38 |  |  |  | 37.7778 | 88.2143
|  | 1:30:pm | 29 | 4.2 | 357 | 7.6 | 3 | 345 | 8 | 363 | 7.8 | 25 | 343 | 23 | 366 | 8 | 43 | 341 | 34 |  |  |  | 41.8605 | 88
Saturday | 2010-09-11 | 9:30:am | 24 | 4.5 | 348 | 7.2 | 3.5 | 355 | 11 | 353 | 7.4 | 33 | 352 | 30 | 356 | 7.6 | 48 | 350 | 43 | 1200 | 57 | 13000 | 31.25 | 89.3939
|  | 11:30:am | 27 | 4.2 | 352 | 7.3 | 3 | 351 | 9 | 357 | 7.5 | 29 | 348 | 27 | 359 | 7.7 | 43 | 346 | 40 |  |  |  | 32.5581 | 89.6552
|  | 1:30:pm | 31 | 4 | 356 | 7.4 | 2.8 | 347 | 6 | 361 | 7.6 | 27 | 345 | 25 | 364 | 7.8 | 40 | 343 | 38 |  |  |  | 32.5 | 89.6296
Sunday | 2010-09-12 | 9:30:am | 27 | 4.2 | 345 | 7.5 | 3.8 | 349 | 14 | 349 | 7.7 | 29 | 347 | 27 | 352 | 7.8 | 53 | 345 | 47 | 1350 | 58 | 12500 | 45.283 | 86.8966
|  | 11:30:am | 30 | 4 | 348 | 7.6 | 3.6 | 344 | 11 | 353 | 7.8 | 23 | 343 | 22 | 357 | 7.9 | 48 | 342 | 44 |  |  |  | 52.0833 | 84.3478
|  | 1:30:pm | 32 | 4.2 | 352 | 7.7 | 3.3 | 341 | 8 | 358 | 7.9 | 20 | 340 | 19 | 360 | 8 | 45 | 338 | 40 |  |  |  | 55.5556 | 83.5
Monday | 2010-09-13 | 9:30:am | 26 | 4.3 | 349 | 7.3 | 4.8 | 357 | 10 | 352 | 7.5 | 36 | 355 | 34 | 356 | 7.6 | 56 | 352 | 45 | 1350 | 55 | 13000 | 35.7143 | 86.6667
|  | 11:30:am | 29 | 4 | 353 | 7.4 | 3 | 355 | 8 | 357 | 7.6 | 33 | 353 | 30 | 360 | 7.7 | 53 | 349 | 42 |  |  |  | 37.7358 | 90.9091
|  | 1:30:pm | 33 | 4 | 359 | 7.5 | 3 | 352 | 5 | 362 | 7.7 | 29 | 350 | 27 | 366 | 7.8 | 50 | 347 | 38 |  |  |  | 42 | 89.6552
Tuesday | 2010-09-14 | 9:30:am | 28 | 4.6 | 353 | 7.4 | 3.9 | 356 | 13 | 356 | 7.6 | 36 | 352 | 31 | 359 | 7.8 | 44 | 349 | 39 | 1200 | 58 | 13000 | 18.1818 | 89.1667
|  | 11:30:am | 30 | 4.3 | 359 | 7.5 | 3.7 | 352 | 10 | 361 | 7.7 | 34 | 350 | 29 | 363 | 7.9 | 41 | 346 | 36 |  |  |  | 17.0732 | 89.1176
|  | 1:30:pm | 32 | 4 | 362 | 7.6 | 3.4 | 349 | 8 | 366 | 7.8 | 32 | 347 | 27 | 369 | 7.9 | 39 | 343 | 33 |  |  |  | 17.9487 | 89.375
Wednesday | 2010-09-15 | 9:30:am | 27 | 4.4 | 344 | 7.2 | 3 | 349 | 14 | 348 | 7.4 | 29 | 345 | 25 | 351 | 7.6 | 61 | 342 | 51 | 1500 | 56 | 12500 | 52.459 | 89.6552
|  | 11:30:am | 29 | 4.2 | 348 | 7.3 | 2.8 | 352 | 11 | 352 | 7.5 | 25 | 348 | 23 | 355 | 7.7 | 57 | 346 | 48 |  |  |  | 56.1404 | 88.8
|  | 1:30:pm | 31 | 4 | 352 | 7.4 | 2.6 | 356 | 8 | 356 | 7.6 | 22 | 353 | 20 | 359 | 7.8 | 52 | 349 | 44 |  |  |  | 57.6923 | 88.1818
Thursday | 2010-09-16 | 9:30:am | 26 | 4.2 | 347 | 7.3 | 3.7 | 348 | 14 | 351 | 7.5 | 40 | 347 | 17 | 355 | 7.7 | 92 | 344 | 57 | 1350 | 58 | 13000 | 56.5217 | 90.75
|  | 11:30:am | 28 | 4 | 351 | 7.4 | 4 | 352 | 11 | 355 | 7.6 | 37 | 350 | 14 | 359 | 7.8 | 88 | 347 | 52 |  |  |  | 57.9545 | 89.1892
|  | 1:30:pm | 32 | 4 | 354 | 7.5 | 3.7 | 355 | 9 | 359 | 7.7 | 35 | 353 | 11 | 364 | 7.9 | 85 | 350 | 46 |  |  |  | 58.8235 | 89.4286
Friday | 2010-09-17 | 9:30:am | 24 | 4.3 | 359 | 7.4 | 4 | 347 | 11 | 362 | 7.6 | 45 | 344 | 31 | 365 | 7.8 | 69 | 341 | 48 | 2250 | 59 | 12500 | 34.7826 | 91.1111
|  | 11:30:am | 26 | 4 | 363 | 7.2 | 3.6 | 351 | 8 | 364 | 7.7 | 43 | 348 | 28 | 368 | 7.9 | 66 | 345 | 44 |  |  |  | 34.8485 | 91.6279
|  | 1:30:pm | 29 | 4 | 367 | 7.3 | 3.2 | 354 | 7 | 369 | 7.8 | 40 | 351 | 25 | 370 | 8 | 62 | 348 | 40 |  |  |  | 35.4839 | 92
Saturday | 2010-09-18 | 9:30:am | 26 | 4.4 | 360 | 7.5 | 3.7 | 353 | 13 | 364 | 7.7 | 49 | 350 | 33 | 367 | 7.8 | 75 | 347 | 56 | 2250 | 57 | 13000 | 34.6667 | 92.449
|  | 11:30:am | 28 | 4.2 | 363 | 7.6 | 3.3 | 357 | 11 | 367 | 7.8 | 52 | 353 | 29 | 369 | 7.9 | 71 | 349 | 52 |  |  |  | 26.7606 | 93.6538
|  | 1:30:pm | 32 | 4 | 366 | 7.7 | 3 | 359 | 8 | 369 | 7.9 | 55 | 356 | 24 | 371 | 7.9 | 74 | 352 | 47 |  |  |  | 25.6757 | 94.5455
Sunday | 2010-09-19 | 9:30:am | 25 | 4.8 | 358 | 7.4 | 3.8 | 347 | 10 | 361 | 7.8 | 44 | 343 | 29 | 363 | 7.9 | 65 | 340 | 48 | 1950 | 58 | 13000 | 32.3077 | 91.3636
|  | 11:30:am | 28 | 4.4 | 361 | 7.3 | 3.6 | 349 | 8 | 366 | 7.8 | 39 | 346 | 26 | 368 | 8 | 62 | 343 | 44 |  |  |  | 37.0968 | 90.7692
|  | 1:30:pm | 33 | 4.2 | 363 | 7.3 | 3.2 | 352 | 6 | 368 | 7.9 | 36 | 349 | 22 | 371 | 8 | 59 | 347 | 40 |  |  |  | 38.9831 | 91.1111
Monday | 2010-09-20 | 9:30:am | 22 | 4.6 | 345 | 7.5 | 4.4 | 345 | 13 | 348 | 7.7 | 41 | 342 | 30 | 352 | 7.8 | 68 | 339 | 43 | 2100 | 59 | 13000 | 39.7059 | 89.2683
|  | 11:30:am | 25 | 4.3 | 349 | 7.6 | 4 | 347 | 11 | 352 | 7.8 | 38 | 344 | 25 | 358 | 7.9 | 63 | 342 | 39 |  |  |  | 39.6825 | 89.4737
|  | 1:30:pm | 28 | 4 | 352 | 7.6 | 3.8 | 351 | 10 | 355 | 7.8 | 33 | 348 | 20 | 360 | 8 | 58 | 346 | 34 |  |  |  | 43.1034 | 88.4848
Tuesday | 2010-09-21 | 9:30:am | 23 | 4.2 | 357 | 7.3 | 4.3 | 354 | 11 | 359 | 7.5 | 36 | 350 | 34 | 364 | 7.7 | 64 | 346 | 45 | 2100 | 57 | 13000 | 43.75 | 88.0556
|  | 11:30:am | 26 | 4 | 360 | 7.4 | 3.9 | 357 | 9 | 363 | 7.6 | 33 | 352 | 30 | 368 | 7.8 | 59 | 348 | 41 |  |  |  | 44.0678 | 88.1818
|  | 1:30:pm | 29 | 4 | 362 | 7.5 | 3.6 | 359 | 7 | 365 | 7.7 | 29 | 356 | 27 | 369 | 7.9 | 53 | 352 | 37 |  |  |  | 45.283 | 87.5862
Wednesday | 2010-09-22 | 9:30:am | 26 | 4.7 | 349 | 7.5 | 3.9 | 343 | 12 | 349 | 7.6 | 42 | 340 | 28 | 353 | 7.7 | 55 | 338 | 54 | 1800 | 50 | 10000 | 23.6364 | 90.7143
|  | 11:30:am | 28 | 4.3 | 354 | 7.6 | 3.6 | 347 | 10 | 353 | 7.7 | 38 | 344 | 25 | 357 | 7.9 | 53 | 341 | 47 |  |  |  | 28.3019 | 90.5263
|  | 1:30:pm | 32 | 4.2 | 359 | 7.7 | 3 | 349 | 8 | 359 | 7.8 | 35 | 347 | 22 | 362 | 8 | 50 | 345 | 44 |  |  |  | 30 | 91.4286
Thursday | 2010-09-23 | 9:30:am | 25 | 4.5 | 351 | 7.3 | 4 | 353 | 10 | 355 | 7.5 | 37 | 349 | 36 | 358 | 7.8 | 39 | 342 | 33 | 1200 | 59 | 13000 | 5.1282 | 89.1892
|  | 11:30:am | 27 | 4.3 | 356 | 7.4 | 3.6 | 356 | 7 | 359 | 7.6 | 32 | 353 | 31 | 362 | 8 | 43 | 347 | 31 |  |  |  | 25.5814 | 88.75
|  | 1:30:pm | 31 | 4 | 359 | 7.5 | 3.3 | 358 | 5 | 363 | 7.7 | 28 | 356 | 28 | 366 | 8 | 45 | 352 | 29 |  |  |  | 37.7778 | 88.2143
Friday | 2010-09-24 | 9:30:am | 27 | 4.4 | 348 | 7.4 | 3.8 | 344 | 12 | 350 | 7.6 | 38 | 348 | 24 | 353 | 7.7 | 64 | 344 | 43 | 1200 | 57 | 13000 | 40.625 | 90
|  | 11:30:am | 29 | 4.2 | 352 | 7.5 | 3.2 | 348 | 15 | 355 | 7.7 | 33 | 351 | 22 | 358 | 7.8 | 60 | 347 | 39 |  |  |  | 45 | 90.303
|  | 1:30:pm | 32 | 4 | 355 | 7.6 | 2.8 | 351 | 11 | 359 | 7.8 | 30 | 355 | 20 | 362 | 7.9 | 57 | 352 | 36 |  |  |  | 47.3684 | 90.6667
Saturday | 2010-09-25 | 9:30:am | 25 | 4.8 | 344 | 7.3 | 4.4 | 351 | 11 | 353 | 7.5 | 32 | 353 | 26 | 356 | 7.7 | 45 | 348 | 37 | 1200 | 55 | 12500 | 28.8889 | 86.25
|  | 11:30:am | 28 | 4.6 | 347 | 7.4 | 3.8 | 355 | 9 | 358 | 7.6 | 28 | 358 | 23 | 362 | 7.8 | 39 | 354 | 33 |  |  |  | 28.2051 | 86.4286
|  | 1:30:pm | 32 | 4.3 | 351 | 7.5 | 3.3 | 358 | 7 | 362 | 7.7 | 25 | 360 | 21 | 366 | 8 | 37 | 358 | 30 |  |  |  | 32.4324 | 86.8
Sunday | 2010-09-26 | 9:30:am | 23 | 4.4 | 348 | 7.4 | 3.4 | 343 | 9 | 350 | 7.6 | 40 | 340 | 29 | 353 | 7.8 | 65 | 338 | 52 | 1800 | 59 | 12500 | 38.4615 | 91.5
|  | 11:30:am | 25 | 4.4 | 355 | 7.5 | 3 | 340 | 7 | 358 | 7.7 | 45 | 338 | 26 | 360 | 7.9 | 69 | 335 | 46 |  |  |  | 34.7826 | 93.3333
|  | 1:30:pm | 29 | 4.2 | 357 | 7.6 | 2.8 | 338 | 5 | 362 | 7.8 | 49 | 335 | 23 | 365 | 8 | 71 | 333 | 41 |  |  |  | 30.9859 | 94.2857
Monday | 2010-09-27 | 9:30:am | 24 | 4 | 342 | 7.3 | 3.5 | 345 | 11 | 346 | 7.5 | 40 | 342 | 29 | 349 | 7.7 | 59 | 340 | 34 | 1800 | 58 | 13000 | 32.2034 | 91.25
|  | 11:30:am | 27 | 4 | 346 | 7.4 | 3 | 348 | 9 | 349 | 7.6 | 36 | 345 | 25 | 353 | 7.8 | 63 | 342 | 31 |  |  |  | 42.8571 | 91.6667
|  | 1:30:pm | 30 | 4 | 348 | 7.5 | 2.7 | 351 | 7 | 353 | 7.7 | 31 | 349 | 22 | 357 | 7.9 | 55 | 345 | 29 |  |  |  | 43.6364 | 91.2903
Tuesday | 2010-09-28 | 9:30:am | 26 | 4 | 346 | 7.4 | 4 | 343 | 10 | 349 | 7.6 | 30 | 345 | 22 | 353 | 7.8 | 57 | 342 | 30 | 1350 | 59 | 12500 | 47.3684 | 86.6667
|  | 11:30:am | 29 | 4.2 | 349 | 7.5 | 3.4 | 346 | 8 | 352 | 7.7 | 27 | 342 | 21 | 357 | 7.9 | 59 | 339 | 28 |  |  |  | 54.2373 | 87.4074
|  | 1:30:pm | 30 | 4 | 353 | 7.6 | 3 | 349 | 6 | 357 | 7.8 | 24 | 341 | 19 | 362 | 8 | 58 | 336 | 26 |  |  |  | 58.6207 | 87.5
Wednesday | 2010-09-29 | 9:30:am | 26 | 4.3 | 351 | 7.3 | 3.9 | 350 | 9 | 355 | 7.5 | 34 | 346 | 28 | 360 | 7.7 | 62 | 342 | 45 | 1800 | 57 | 12500 | 45.1613 | 88.5294
|  | 11:30:am | 28 | 4.4 | 355 | 7.4 | 3.2 | 352 | 12 | 358 | 7.6 | 29 | 355 | 24 | 363 | 7.8 | 57 | 350 | 38 |  |  |  | 49.1228 | 88.9655
|  | 1:30:pm | 32 | 4.5 | 358 | 7.5 | 2.8 | 355 | 11 | 363 | 7.7 | 25 | 359 | 21 | 367 | 7.9 | 51 | 354 | 35 |  |  |  | 50.9804 | 88.8
Thursday | 2010-09-30 | 9:30:am | 25 | 4.3 | 344 | 7.2 | 3.3 | 345 | 10 | 349 | 7.4 | 31 | 349 | 27 | 353 | 7.6 | 48 | 344 | 33 | 1200 | 60 | 12500 | 35.4167 | 89.3548
|  | 11:30:am | 28 | 4.4 | 348 | 7.4 | 3 | 348 | 9 | 353 | 7.5 | 28 | 354 | 23 | 357 | 7.7 | 45 | 348 | 30 |  |  |  | 37.7778 | 89.2857
|  | 1:30:pm | 31 | 4.5 | 352 | 7.5 | 2.6 | 351 | 7 | 356 | 7.6 | 24 | 357 | 20 | 362 | 7.8 | 43 | 353 | 26 |  |  |  | 44.186 | 89.1667

## 10
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-10-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr)
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | S-R | S-SUP
Friday | 2010-10-01 | 9:30:am | 24 | 4.3 | 344 | 7.3 | 3.4 | 348 | 10 | 349 | 7.5 | 26 | 344 | 21 | 353 | 7.7 | 43 | 340 | 31 | 1500 | 54 | 12500 | 39.5349 | 86.9231
|  | 11:30:am | 27 | 4 | 347 | 7.4 | 3.2 | 352 | 8 | 355 | 7.6 | 23 | 347 | 18 | 359 | 7.8 | 40 | 343 | 28 |  |  |  | 42.5 | 86.087
|  | 1:30:pm | 29 | 4 | 351 | 7.5 | 2.7 | 356 | 6 | 359 | 7.7 | 20 | 353 | 16 | 369 | 7.9 | 37 | 348 | 25 |  |  |  | 45.9459 | 86.5
Saturday | 2010-10-02 | 9:30:am | 23 | 4.6 | 349 | 7.4 | 4 | 344 | 8 | 353 | 7.6 | 29 | 348 | 23 | 357 | 7.8 | 49 | 343 | 32 | 1500 | 58 | 13000 | 40.8163 | 86.2069
|  | 11:30:am | 26 | 4.2 | 352 | 7.5 | 3.6 | 348 | 6 | 358 | 7.7 | 26 | 353 | 20 | 362 | 7.9 | 44 | 347 | 26 |  |  |  | 40.9091 | 86.1538
|  | 1:30:pm | 28 | 4 | 358 | 7.6 | 3.1 | 354 | 5 | 362 | 7.8 | 21 | 359 | 17 | 368 | 8 | 41 | 353 | 22 |  |  |  | 48.7805 | 85.2381
Sunday | 2010-10-03 | 9:30:am | 22 | 4.3 | 344 | 7.2 | 4 | 348 | 9 | 348 | 7.4 | 27 | 350 | 20 | 352 | 7.6 | 47 | 347 | 35 | 1500 | 59 | 13000 | 42.5532 | 85.1852
|  | 11:30:am | 26 | 4 | 348 | 7.3 | 3.6 | 352 | 7 | 353 | 7.5 | 23 | 356 | 18 | 358 | 7.7 | 53 | 352 | 38 |  |  |  | 56.6038 | 84.3478
|  | 1:30:pm | 29 | 4 | 353 | 7.4 | 3 | 357 | 6 | 358 | 7.6 | 20 | 362 | 14 | 362 | 7.8 | 59 | 358 | 40 |  |  |  | 66.1017 | 85
Monday | 2010-10-04 | 9:30:am | 23 | 4.4 | 348 | 7.3 | 3.8 | 352 | 8 | 352 | 7.5 | 42 | 344 | 29 | 356 | 7.7 | 137 | 341 | 59 | 2700 | 56 | 12500 | 69.3431 | 90.9524
|  | 11:30:am | 26 | 4.2 | 353 | 7.4 | 3.3 | 355 | 6 | 356 | 7.6 | 45 | 349 | 23 | 360 | 7.8 | 132 | 346 | 51 |  |  |  | 65.9091 | 92.6667
|  | 1:30:pm | 28 | 4 | 357 | 7.5 | 2.9 | 358 | 5 | 359 | 7.7 | 48 | 353 | 20 | 363 | 7.9 | 126 | 353 | 47 |  |  |  | 61.9048 | 93.9583
Tuesday | 2010-10-05 | 9:30:am | 22 | 4.3 | 345 | 7.3 | 3.6 | 347 | 10 | 348 | 7.5 | 24 | 343 | 21 | 353 | 7.7 | 114 | 341 | 44 | 2250 | 58 | 13000 | 78.9474 | 85
|  | 11:30:am | 25 | 4 | 348 | 7.4 | 3.3 | 350 | 8 | 351 | 7.6 | 22 | 347 | 18 | 355 | 7.8 | 118 | 343 | 48 |  |  |  | 81.3559 | 85
|  | 1:30:pm | 27 | 4 | 351 | 7.5 | 2.9 | 353 | 6 | 354 | 7.7 | 18 | 350 | 15 | 359 | 7.9 | 95 | 345 | 41 |  |  |  | 81.0526 | 83.8889
Wednesday | 2010-10-06 | 9:30:am | 21 | 4.3 | 341 | 7.3 | 2.9 | 345 | 9 | 344 | 7.5 | 24 | 342 | 21 | 349 | 7.6 | 56 | 340 | 34 | 1500 | 56 | 13000 | 57.1429 | 87.9167
|  | 11:30:am | 23 | 4 | 345 | 7.4 | 2.5 | 348 | 7 | 349 | 7.6 | 21 | 344 | 18 | 354 | 7.7 | 53 | 342 | 28 |  |  |  | 60.3774 | 88.0952
|  | 1:30:pm | 25 | 4 | 349 | 7.5 | 2.3 | 351 | 5 | 352 | 7.7 | 17 | 349 | 15 | 358 | 7.8 | 50 | 347 | 25 |  |  |  | 66 | 86.4706
Thursday | 2010-10-07 | 9:30:am | 23 | 4.4 | 346 | 7.4 | 3.9 | 349 | 11 | 350 | 7.6 | 31 | 344 | 27 | 354 | 7.8 | 59 | 342 | 39 | 1650 | 59 | 13000 | 47.4576 | 87.4194
|  | 11:30:am | 26 | 4.2 | 349 | 7.5 | 3.3 | 353 | 9 | 352 | 7.7 | 28 | 347 | 23 | 358 | 7.9 | 62 | 345 | 35 |  |  |  | 54.8387 | 88.2143
|  | 1:30:pm | 29 | 4 | 353 | 7.6 | 3 | 355 | 7 | 358 | 7.8 | 26 | 351 | 20 | 363 | 8 | 66 | 348 | 31 |  |  |  | 60.6061 | 88.4615
Friday | 2010-10-08 | 9:30:am | 23 | 4.4 | 338 | 7.3 | 3 | 345 | 8 | 341 | 7.5 | 23 | 342 | 17 | 345 | 7.7 | 31 | 340 | 25 | 1050 | 58 | 12500 | 25.8065 | 86.9565
|  | 11:30:am | 27 | 4.2 | 343 | 7.4 | 2.8 | 348 | 6 | 345 | 7.6 | 20 | 345 | 15 | 348 | 7.8 | 29 | 342 | 22 |  |  |  | 31.0345 | 86
|  | 1:30:pm | 31 | 4 | 347 | 7.5 | 2.5 | 350 | 4 | 349 | 7.7 | 17 | 347 | 13 | 353 | 7.9 | 27 | 345 | 20 |  |  |  | 37.037 | 85.2941
Saturday | 2010-10-09 | 9:30:am | 24 | 4.5 | 336 | 7.4 | 2.9 | 343 | 10 | 339 | 7.6 | 21 | 338 | 18 | 343 | 7.8 | 28 | 335 | 23 | 900 | 57 | 12500 | 25 | 86.1905
|  | 11:30:am | 28 | 4.3 | 342 | 7.5 | 2.5 | 346 | 7 | 344 | 7.7 | 17 | 342 | 16 | 348 | 7.9 | 25 | 338 | 20 |  |  |  | 32 | 85.2941
|  | 1:30:pm | 33 | 4 | 346 | 7.6 | 2.3 | 348 | 5 | 349 | 7.8 | 14 | 345 | 13 | 353 | 8 | 22 | 340 | 18 |  |  |  | 36.3636 | 83.5714
Sunday | 2010-10-10 | 9:30:am | 22 | 4.2 | 342 | 7.2 | 3.3 | 341 | 7 | 346 | 7.4 | 18 | 337 | 15 | 349 | 7.6 | 31 | 334 | 25 | 1050 | 59 | 12500 | 41.9355 | 81.6667
|  | 11:30:am | 26 | 4 | 347 | 7.3 | 3 | 345 | 5 | 350 | 7.5 | 15 | 341 | 12 | 354 | 7.7 | 32 | 338 | 22 |  |  |  | 53.125 | 80
|  | 1:30:pm | 29 | 4 | 349 | 7.4 | 2.5 | 348 | 2 | 353 | 7.6 | 13 | 345 | 10 | 356 | 7.8 | 29 | 342 | 20 |  |  |  | 55.1724 | 80.7692
Monday | 2010-10-11 | 9:30:am | 21 | 4 | 343 | 7.3 | 3.5 | 338 | 8 | 346 | 7.5 | 22 | 333 | 18 | 348 | 7.7 | 35 | 330 | 32 | 1050 | 57 | 13000 | 37.1429 | 84.0909
|  | 11:30:am | 23 | 4 | 346 | 7.4 | 3 | 343 | 6 | 350 | 7.6 | 18 | 337 | 15 | 354 | 7.8 | 31 | 333 | 29 |  |  |  | 41.9355 | 83.3333
|  | 1:30:pm | 25 | 4 | 349 | 7.5 | 2.8 | 348 | 4 | 354 | 7.7 | 14 | 342 | 13 | 358 | 7.9 | 29 | 338 | 25 |  |  |  | 51.7241 | 80
Tuesday | 2010-10-12 | 9:30:am | 24 | 4.8 | 343 | 7.4 | 3 | 333 | 5 | 347 | 7.6 | 15 | 330 | 11 | 350 | 7.7 | 25 | 326 | 21 | 450 | 58 | 12500 | 40 | 80
|  | 11:30:am | 27 | 4.4 | 338 | 7.5 | 2.7 | 330 | 3 | 333 | 7.7 | 12 | 324 | 8 | 342 | 7.8 | 22 | 320 | 18 |  |  |  | 45.4545 | 77.5
|  | 1:30:pm | 29 | 4.2 | 335 | 7.6 | 2.4 | 325 | 2 | 330 | 7.8 | 10 | 320 | 6 | 338 | 7.9 | 20 | 315 | 15 |  |  |  | 50 | 76
Wednesday | 2010-10-13 | 9:30:am | 26 | 4 | 333 | 7.3 | 1.9 | 318 | 4 | 329 | 7.5 | 16 | 314 | 10 | 325 | 7.7 | 22 | 310 | 17 | _ | 55 | 13000 | 27.2727 | 88.125
|  | 11:30:am | 28 | 4 | 330 | 7.4 | 1.5 | 315 | 2 | 324 | 7.6 | 12 | 311 | 7 | 321 | 7.8 | 18 | 308 | 13 |  |  |  | 33.3333 | 87.5
|  | 1:30:pm | 31 | 4 | 328 | 7.5 | 1.2 | 310 | 1 | 320 | 7.7 | 11 | 308 | 5 | 317 | 7.9 | 17 | 300 | 10 |  |  |  | 35.2941 | 89.0909
Thursday | 2010-10-14 | 9:30:am | 22 | 4.3 | 299 | 7.4 | 3.3 | 264 | 5 | 303 | 7.5 | 21 | 260 | 17 | 307 | 7.7 | 55 | 255 | 37 | 1050 | 58 | 13000 | 61.8182 | 84.2857
|  | 11:30:am | 24 | 4 | 296 | 7.5 | 3 | 259 | 3 | 299 | 7.6 | 17 | 255 | 13 | 303 | 7.8 | 44 | 251 | 31 |  |  |  | 61.3636 | 82.3529
|  | 1:30:pm | 26 | 4 | 290 | 7.6 | 2.8 | 253 | 2 | 293 | 7.7 | 13 | 249 | 10 | 300 | 7.9 | 36 | 247 | 26 |  |  |  | 63.8889 | 78.4615
Friday | 2010-10-15 | 9:30:am | 21 | 4.4 | 293 | 7.5 | 3 | 255 | 7 | 297 | 7.7 | 23 | 249 | 18 | 306 | 7.8 | 43 | 244 | 29 | 900 | 56 | 12500 | 46.5116 | 86.9565
|  | 11:30:am | 24 | 4.2 | 288 | 7.6 | 2.7 | 250 | 5 | 294 | 7.8 | 21 | 245 | 15 | 300 | 7.9 | 37 | 241 | 23 |  |  |  | 43.2432 | 87.1429
|  | 1:30:pm | 27 | 4 | 284 | 7.7 | 2.2 | 244 | 3 | 287 | 7.8 | 18 | 240 | 11 | 294 | 8 | 33 | 237 | 20 |  |  |  | 45.4545 | 87.7778
Saturday | 2010-10-16 | 9:30:am | 24 | 4.6 | 290 | 7.4 | 2.8 | 247 | 9 | 295 | 7.6 | 21 | 243 | 16 | 299 | 7.8 | 37 | 240 | 27 | 900 | 58 | 13000 | 43.2432 | 86.6667
|  | 11:30:am | 27 | 4.3 | 284 | 7.5 | 2.6 | 241 | 7 | 290 | 7.7 | 17 | 239 | 11 | 293 | 7.9 | 33 | 235 | 25 |  |  |  | 48.4848 | 84.7059
|  | 1:30:pm | 30 | 4 | 280 | 7.6 | 2.2 | 234 | 4 | 284 | 7.8 | 14 | 231 | 9 | 286 | 8 | 31 | 227 | 22 |  |  |  | 54.8387 | 84.2857
Sunday | 2010-10-17 | 9:30:am | 22 | 4.4 | 288 | 7.3 | 2.5 | 240 | 7 | 289 | 7.5 | 18 | 236 | 15 | 296 | 7.6 | 22 | 233 | 18 | _ | 59 | 12500 | 18.1818 | 86.1111
|  | 11:30:am | 25 | 4.2 | 285 | 7.4 | 2 | 233 | 4 | 287 | 7.6 | 15 | 231 | 12 | 292 | 7.7 | 18 | 228 | 15 |  |  |  | 16.6667 | 86.6667
|  | 1:30:pm | 27 | 4 | 281 | 7.5 | 1.7 | 226 | 2 | 283 | 7.7 | 12 | 224 | 8 | 287 | 7.8 | 16 | 222 | 13 |  |  |  | 25 | 85.8333
Monday | 2010-10-18 | 9:30:am | 24 | 4.2 | 286 | 7.5 | 3 | 231 | 8 | 290 | 7.6 | 23 | 228 | 17 | 295 | 7.7 | 33 | 225 | 20 | 450 | 57 | 13000 | 30.303 | 86.9565
|  | 11:30:am | 27 | 4 | 280 | 7.6 | 2.7 | 225 | 6 | 285 | 7.7 | 20 | 222 | 14 | 290 | 7.8 | 30 | 220 | 17 |  |  |  | 33.3333 | 86.5
|  | 1:30:pm | 31 | 4 | 277 | 7.7 | 2.3 | 214 | 4 | 280 | 7.8 | 17 | 212 | 12 | 285 | 8 | 24 | 210 | 15 |  |  |  | 29.1667 | 86.4706
Tuesday | 2010-10-19 | 9:30:am | 23 | 4 | 278 | 7.6 | 3.2 | 222 | 6 | 283 | 7.7 | 24 | 220 | 19 | 289 | 7.9 | 28 | 215 | 20 | 450 | 58 | 13000 | 14.2857 | 86.6667
|  | 11:30:am | 25 | 4 | 273 | 7.6 | 2.9 | 216 | 4 | 278 | 7.7 | 20 | 213 | 15 | 284 | 8 | 25 | 211 | 17 |  |  |  | 20 | 85.5
|  | 1:30:pm | 27 | 4 | 270 | 7.7 | 2.6 | 208 | 2 | 272 | 7.8 | 17 | 204 | 11 | 279 | 8 | 22 | 202 | 14 |  |  |  | 22.7273 | 84.7059
Wednesday | 2010-10-20 | 9:30:am | 25 | 4.2 | 275 | 7.4 | 3.8 | 225 | 5 | 282 | 7.5 | 20 | 221 | 15 | 288 | 7.6 | 24 | 218 | 18 | _ | 59 | 13000 | 16.6667 | 81
|  | 11:30:am | 28 | 4 | 270 | 7.5 | 3.3 | 218 | 3 | 277 | 7.6 | 17 | 214 | 11 | 282 | 7.8 | 21 | 211 | 15 |  |  |  | 19.0476 | 80.5882
|  | 1:30:pm | 32 | 4 | 268 | 7.6 | 3 | 208 | 1 | 272 | 7.7 | 14 | 203 | 9 | 277 | 7.9 | 19 | 200 | 12 |  |  |  | 26.3158 | 78.5714
Thursday | 2010-10-21 | 9:30:am | 23 | 4.4 | 244 | 7.3 | 2.6 | 210 | 4 | 248 | 7.4 | 21 | 207 | 14 | 251 | 7.5 | 28 | 202 | 15 | _ | 57 | 13000 | 25 | 87.619
|  | 11:30:am | 26 | 4.2 | 247 | 7.4 | 2.2 | 205 | 3 | 253 | 7.6 | 17 | 203 | 11 | 255 | 7.6 | 24 | 198 | 12 |  |  |  | 29.1667 | 87.0588
|  | 1:30:pm | 28 | 4 | 251 | 7.5 | 1.8 | 200 | 1 | 256 | 7.7 | 14 | 198 | 10 | 259 | 7.7 | 22 | 194 | 11 |  |  |  | 36.3636 | 87.1429
Friday | 2010-10-22 | 9:30:am | 22 | 4.6 | 237 | 7.5 | 2.9 | 206 | 5 | 240 | 7.6 | 24 | 202 | 12 | 243 | 7.7 | 29 | 200 | 18 | _ | 50 | 10000 | 17.2414 | 87.9167
|  | 11:30:am | 25 | 4.3 | 240 | 7.6 | 2.7 | 200 | 2 | 243 | 7.7 | 21 | 196 | 10 | 246 | 7.8 | 26 | 194 | 15 |  |  |  | 19.2308 | 87.1429
|  | 1:30:pm | 29 | 4 | 243 | 7.7 | 2.4 | 195 | 1 | 246 | 7.8 | 18 | 193 | 8 | 249 | 7.9 | 23 | 190 | 12 |  |  |  | 21.7391 | 86.6667
Saturday | 2010-10-23 | 9:30:am | 21 | 4.3 | 233 | 7.4 | 3 | 199 | 3 | 237 | 7.5 | 22 | 195 | 16 | 240 | 7.6 | 27 | 191 | 19 | _ | 59 | 13000 | 18.5185 | 86.3636
|  | 11:30:am | 24 | 4 | 236 | 7.5 | 2.7 | 193 | 2 | 239 | 7.6 | 19 | 192 | 12 | 242 | 7.7 | 23 | 188 | 16 |  |  |  | 17.3913 | 85.7895
|  | 1:30:pm | 27 | 4 | 239 | 7.6 | 2.3 | 187 | 2 | 242 | 7.7 | 16 | 184 | 10 | 245 | 7.8 | 22 | 181 | 13 |  |  |  | 27.2727 | 85.625
Sunday | 2010-10-24 | 9:30:am | 23 | 4 | 231 | 7.3 | 3.3 | 197 | 4 | 234 | 7.4 | 25 | 192 | 13 | 238 | 7.6 | 28 | 188 | 16 | _ | 57 | 13000 | 10.7143 | 86.8
|  | 11:30:am | 25 | 4 | 234 | 7.4 | 3 | 191 | 2 | 237 | 7.5 | 21 | 188 | 10 | 241 | 7.7 | 25 | 185 | 12 |  |  |  | 16 | 85.7143
|  | 1:30:pm | 28 | 4 | 237 | 7.5 | 2.7 | 184 | 1 | 240 | 7.6 | 18 | 181 | 7 | 245 | 7.8 | 23 | 180 | 10 |  |  |  | 21.7391 | 85
Monday | 2010-10-25 | 9:30:am | 22 | 4.2 | 228 | 7.4 | 3.4 | 192 | 2 | 231 | 7.5 | 24 | 188 | 11 | 234 | 7.6 | 32 | 184 | 21 | _ | 55 | 12500 | 25 | 85.8333
|  | 11:30:am | 25 | 4 | 232 | 7.5 | 3 | 195 | 1 | 235 | 7.6 | 27 | 193 | 9 | 238 | 7.7 | 35 | 188 | 22 |  |  |  | 22.8571 | 88.8889
|  | 1:30:pm | 28 | 4 | 236 | 7.6 | 2.6 | 197 | 1 | 239 | 7.7 | 29 | 196 | 7 | 242 | 7.8 | 33 | 192 | 25 |  |  |  | 12.1212 | 91.0345
Tuesday | 2010-10-26 | 9:30:am | [18 empty] | 59 | 12500 | #DIV/0! | #DIV/0! | bar: EC to PH; TDS to AFTER SEDIMENTATION PH; AFTER SEDIMENTATION TDS to RAW (INLET WATER) PH; RAW (INLET WATER) TDS to RAW (INLET WATER) TSS
|  | 11:30:am | [20 empty] | #DIV/0! | #DIV/0! | bar: EC to PH; TDS to AFTER SEDIMENTATION PH; AFTER SEDIMENTATION TDS to RAW (INLET WATER) PH; RAW (INLET WATER) TDS to RAW (INLET WATER) TSS
|  | 1:30:pm | [20 empty] | #DIV/0! | #DIV/0! | bar: EC to PH; TDS to AFTER SEDIMENTATION PH; AFTER SEDIMENTATION TDS to RAW (INLET WATER) PH; RAW (INLET WATER) TDS to RAW (INLET WATER) TSS
Wednesday | 2010-10-27 | 9:30:am | 24 | 4 | 233 | 7.3 | 2.9 | 245 | 8 | 238 | 7.5 | 33 | 241 | 23 | 243 | 7.7 | 45 | 237 | 38 | 900 | 58 | 13000 | 26.6667 | 91.2121
|  | 11:30:am | 27 | 4 | 237 | 7.4 | 2.5 | 249 | 6 | 241 | 7.6 | 30 | 245 | 20 | 246 | 7.8 | 42 | 241 | 33 |  |  |  | 28.5714 | 91.6667
|  | 1:30:pm | 29 | 4 | 239 | 7.5 | 2.2 | 251 | 5 | 245 | 7.7 | 28 | 248 | 17 | 253 | 7.9 | 40 | 245 | 27 |  |  |  | 30 | 92.1429
Thursday | 2010-10-28 | 9:30:am | 22 | 4.3 | 266 | 7.4 | 2.7 | 239 | 6 | 269 | 7.5 | 21 | 235 | 14 | 272 | 7.6 | 25 | 231 | 15 | _ | 59 | 12500 | 16 | 87.1429
|  | 11:30:am | 24 | 4 | 260 | 7.5 | 2.2 | 233 | 3 | 265 | 7.6 | 18 | 230 | 11 | 267 | 7.7 | 23 | 228 | 12 |  |  |  | 21.7391 | 87.7778
|  | 1:30:pm | 26 | 4 | 255 | 7.6 | 2 | 227 | 1 | 261 | 7.7 | 15 | 225 | 8 | 264 | 7.8 | 20 | 222 | 10 |  |  |  | 25 | 86.6667
Friday | 2010-10-29 | 9:30:am | 21 | 4.5 | 254 | 7.5 | 2.5 | 239 | 7 | 250 | 7.6 | 17 | 235 | 12 | 253 | 7.7 | 23 | 230 | 13 | _ | 57 | 12500 | 26.087 | 85.2941
|  | 11:30:am | 23 | 4.2 | 250 | 7.6 | 2.2 | 223 | 4 | 248 | 7.7 | 14 | 220 | 10 | 255 | 7.8 | 20 | 218 | 10 |  |  |  | 30 | 84.2857
|  | 1:30:pm | 26 | 4 | 246 | 7.7 | 1.8 | 221 | 2 | 244 | 7.8 | 11 | 217 | 7 | 251 | 7.9 | 18 | 215 | 8 |  |  |  | 38.8889 | 83.6364
Saturday | 2010-10-30 | 9:30:am | 23 | 4.4 | 243 | 7.4 | 2.9 | 235 | 8 | 239 | 7.5 | 19 | 231 | 11 | 242 | 7.6 | 24 | 227 | 15 | _ | 60 | 12500 | 20.8333 | 84.7368
|  | 11:30:am | 25 | 4.2 | 240 | 7.5 | 2.5 | 229 | 6 | 236 | 7.6 | 15 | 227 | 9 | 239 | 7.7 | 21 | 222 | 11 |  |  |  | 28.5714 | 83.3333
|  | 1:30:pm | 27 | 4 | 237 | 7.6 | 2.2 | 224 | 3 | 233 | 7.7 | 13 | 222 | 7 | 236 | 7.8 | 18 | 217 | 8 |  |  |  | 27.7778 | 83.0769
Sunday | 2010-10-31 | 9:30 | 21 | 4.3 | 238 | 7.6 | 3 | 232 | 5 | 234 | 7.7 | 16 | 228 | 12 | 238 | 7.8 | 22 | 222 | 12 | _ | 59 | 12500 | 27.2727 | 81.25
|  | 11:30 | 24 | 4 | 235 | 7.7 | 2.7 | 228 | 3 | 232 | 7.8 | 13 | 225 | 9 | 235 | 7.9 | 20 | 217 | 9 |  |  |  | 35 | 79.2308
|  | 1:30:pm | 26 | 4 | 232 | 7.7 | 2.5 | 223 | 1 | 229 | 7.8 | 11 | 221 | 6 | 232 | 8 | 17 | 215 | 7 |  |  |  | 35.2941 | 77.2727

## 11
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-11-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr)
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | S-R | S-SUP
Monday | 2010-11-01 | 9:30:am | 21 | 4.3 | 228 | 7.4 | 2.2 | 212 | 4 | 231 | 7.5 | 12 | 209 | 9 | 233 | 7.7 | 20 | 204 | 14 | _ | 54 | 12500 | 40 | 81.6667
|  | 11:30:am | 23 | 4 | 223 | 7.5 | 1.8 | 207 | 2 | 228 | 7.6 | 10 | 205 | 7 | 231 | 7.8 | 18 | 200 | 11 |  |  |  | 44.4444 | 82
|  | 1:30:pm | 25 | 4 | 221 | 7.6 | 1.5 | 201 | 1 | 225 | 7.7 | 8 | 200 | 5 | 228 | 7.9 | 15 | 196 | 10 |  |  |  | 46.6667 | 81.25
Tuesday | 2010-11-02 | 9:30:am | 23 | 4.4 | 222 | 7.5 | 2.8 | 208 | 5 | 226 | 7.6 | 13 | 205 | 8 | 229 | 7.7 | 18 | 200 | 13 | _ | 58 | 13000 | 27.7778 | 78.4615
|  | 11:30:am | 26 | 4.2 | 218 | 7.6 | 2.5 | 206 | 3 | 221 | 7.7 | 10 | 201 | 6 | 225 | 7.8 | 15 | 196 | 10 |  |  |  | 33.3333 | 75
|  | 1:30:pm | 28 | 4 | 215 | 7.7 | 2.2 | 203 | 2 | 218 | 7.8 | 9 | 197 | 4 | 222 | 7.9 | 14 | 192 | 8 |  |  |  | 35.7143 | 75.5556
Wednesday | 2010-11-03 | 9:30:am | 22 | 4 | 219 | 7.4 | 2.4 | 211 | 3 | 222 | 7.4 | 12 | 207 | 6 | 227 | 7.6 | 18 | 202 | 11 | _ | 59 | 13000 | 33.3333 | 80
|  | 11:30:am | 24 | 4 | 215 | 7.5 | 2.1 | 208 | 3 | 220 | 7.5 | 10 | 204 | 3 | 223 | 7.7 | 15 | 200 | 9 |  |  |  | 33.3333 | 79
|  | 1:30:pm | 26 | 4 | 211 | 7.6 | 1.7 | 204 | 1 | 216 | 7.7 | 9 | 200 | 1 | 219 | 7.8 | 12 | 196 | 7 |  |  |  | 25 | 81.1111
Thursday | 2010-11-04 | 9:30:am | 23 | 4.3 | 210 | 7.5 | 3.6 | 210 | 4 | 215 | 7.7 | 13 | 205 | 9 | 220 | 7.8 | 18 | 200 | 11 | _ | 56 | 12500 | 27.7778 | 72.3077
|  | 11:30:am | 25 | 4 | 206 | 7.6 | 3 | 205 | 2 | 211 | 7.7 | 10 | 200 | 7 | 216 | 7.8 | 15 | 196 | 9 |  |  |  | 33.3333 | 70
|  | 1:30:pm | 27 | 4 | 200 | 7.7 | 2.6 | 200 | 1 | 207 | 7.8 | 9 | 194 | 5 | 211 | 7.9 | 13 | 190 | 7 |  |  |  | 30.7692 | 71.1111
Friday | 2010-11-05 | 9:30:am | 21 | 4.4 | 198 | 7.4 | 2.2 | 196 | 2 | 202 | 7.6 | 11 | 192 | 7 | 208 | 7.7 | 17 | 188 | 11 | _ | 58 | 13000 | 35.2941 | 80
|  | 11:30:am | 24 | 4.2 | 192 | 7.5 | 2 | 193 | 1 | 197 | 7.7 | 9 | 188 | 5 | 204 | 7.8 | 15 | 184 | 9 |  |  |  | 40 | 77.7778
|  | 1:30:pm | 27 | 4 | 190 | 7.6 | 1.7 | 188 | 1 | 193 | 7.8 | 6 | 183 | 3 | 200 | 7.9 | 12 | 180 | 7 |  |  |  | 50 | 71.6667
Saturday | 2010-11-06 | 9:30:am | 23 | 4.2 | 195 | 7.3 | 2 | 190 | 3.5 | 199 | 7.5 | 10 | 184 | 8 | 205 | 7.7 | 17 | 180 | 13 | _ | 56 | 13000 | 41.1765 | 80
|  | 11:30:am | 25 | 4 | 190 | 7.4 | 1.7 | 186 | 2.2 | 194 | 7.6 | 8 | 180 | 6 | 200 | 7.8 | 15 | 177 | 11 |  |  |  | 46.6667 | 78.75
|  | 1:30:pm | 28 | 4 | 187 | 7.5 | 1.3 | 180 | 1.8 | 190 | 7.7 | 6 | 177 | 4 | 196 | 7.8 | 11 | 173 | 9 |  |  |  | 45.4545 | 78.3333
Sunday | 2010-11-07 | 9:30:am | 22 | 4 | 198 | 7.4 | 2.3 | 205 | 3 | 201 | 7.6 | 11 | 200 | 7 | 206 | 7.8 | 15 | 197 | 11 | _ | 59 | 13000 | 26.6667 | 79.0909
|  | 11:30:am | 24 | 4 | 193 | 7.5 | 2 | 200 | 1 | 197 | 7.7 | 9 | 194 | 5 | 203 | 7.9 | 13 | 192 | 9 |  |  |  | 30.7692 | 77.7778
|  | 1:30:pm | 26 | 4 | 190 | 7.6 | 1.6 | 196 | 1 | 192 | 7.8 | 8 | 190 | 4 | 199 | 8 | 11 | 188 | 7 |  |  |  | 27.2727 | 80
Monday | 2010-11-08 | 9:30:am | 23 | 4.2 | 188 | 7.4 | 2.7 | 182 | 2 | 191 | 7.5 | 10 | 177 | 5 | 195 | 7.7 | 15 | 173 | 9 | _ | 58 | 12500 | 33.3333 | 73
|  | 11:30:am | 26 | 4.2 | 183 | 7.5 | 2.2 | 178 | 1 | 188 | 7.6 | 7 | 173 | 3 | 190 | 7.8 | 12 | 170 | 7 |  |  |  | 41.6667 | 68.5714
|  | 1:30:pm | 29 | 4 | 180 | 7.6 | 1.5 | 172 | 1 | 183 | 7.7 | 5 | 169 | 2 | 188 | 7.9 | 10 | 166 | 6 |  |  |  | 50 | 70
Tuesday | 2010-11-09 | 9:30:am | 22 | 4.3 | 188 | 7.3 | 2.8 | 175 | 2 | 193 | 7.4 | 10 | 170 | 4 | 196 | 7.5 | 14 | 167 | 8 | _ | 57 | 12500 | 28.5714 | 72
|  | 11:30:am | 24 | 4 | 185 | 7.4 | 2.5 | 170 | 1 | 189 | 7.5 | 8 | 167 | 3 | 192 | 7.6 | 12 | 163 | 6 |  |  |  | 33.3333 | 68.75
|  | 1:30:pm | 26 | 4 | 182 | 7.5 | 2.2 | 168 | 1 | 185 | 7.6 | 6 | 163 | 2 | 188 | 7.7 | 10 | 159 | 5 |  |  |  | 40 | 63.3333
Wednesday | 2010-11-10 | 9:30:am | 23 | 4 | 185 | 7.4 | 2 | 172 | 3 | 191 | 7.5 | 8 | 168 | 5 | 195 | 7.6 | 12 | 163 | 9 | _ | 59 | 12500 | 33.3333 | 75
|  | 11:30:am | 27 | 4 | 180 | 7.5 | 1.7 | 170 | 2 | 186 | 7.6 | 7 | 164 | 4 | 190 | 7.7 | 10 | 158 | 7 |  |  |  | 30 | 75.7143
|  | 1:30:pm | 29 | 4 | 178 | 7.6 | 1.3 | 166 | 1 | 182 | 7.7 | 6 | 160 | 3 | 183 | 7.8 | 8 | 153 | 5 |  |  |  | 25 | 78.3333
Thursday | 2010-11-11 | 9:30:am | 24 | 4.4 | 189 | 7.3 | 1.9 | 165 | 2 | 193 | 7.5 | 18 | 161 | 10 | 196 | 7.7 | 25 | 157 | 12 | _ | 57 | 13000 | 28 | 89.4444
|  | 11:30:am | 28 | 4.2 | 184 | 7.4 | 1.5 | 160 | 1 | 190 | 7.6 | 15 | 154 | 8 | 192 | 7.8 | 22 | 150 | 10 |  |  |  | 31.8182 | 90
|  | 1:30:pm | 30 | 4 | 180 | 7.5 | 1.3 | 158 | 1 | 183 | 7.7 | 12 | 150 | 7 | 188 | 7.9 | 20 | 146 | 9 |  |  |  | 40 | 89.1667
Friday | 2010-11-12 | 9:30:am | 21 | 4.3 | 186 | 7.5 | 2 | 168 | 1 | 190 | 7.6 | 16 | 162 | 12 | 194 | 7.7 | 26 | 157 | 16 | _ | 58 | 12500 | 38.4615 | 87.5
|  | 11:30:am | 24 | 4 | 180 | 7.6 | 1.7 | 165 | 1 | 185 | 7.7 | 12 | 158 | 10 | 190 | 7.8 | 23 | 152 | 13 |  |  |  | 47.8261 | 85.8333
|  | 1:30:pm | 27 | 4 | 178 | 7.7 | 1.2 | 162 | 1 | 182 | 7.8 | 10 | 155 | 7 | 185 | 7.9 | 20 | 148 | 11 |  |  |  | 50 | 88
Saturday | 2010-11-13 | 9:30:am | [20 empty] | #REF! | #REF! | bar: EC to PH; TDS to AFTER SEDIMENTATION PH; AFTER SEDIMENTATION TDS to RAW (INLET WATER) PH; RAW (INLET WATER) TDS to RAW (INLET WATER) TSS
|  | 11:30:am | [20 empty] | #REF! | #REF! | bar: EC to PH; TDS to AFTER SEDIMENTATION PH; AFTER SEDIMENTATION TDS to RAW (INLET WATER) PH; RAW (INLET WATER) TDS to RAW (INLET WATER) TSS
|  | 1:30:pm | [20 empty] | #REF! | #REF! | bar: EC to PH; TDS to AFTER SEDIMENTATION PH; AFTER SEDIMENTATION TDS to RAW (INLET WATER) PH; RAW (INLET WATER) TDS to RAW (INLET WATER) TSS
Sunday | 2010-11-14 | 9:30:am | 23 | 4.3 | 165 | 7.4 | 2 | 145 | 4 | 169 | 7.6 | 23 | 148 | 15 | 174 | 7.8 | 32 | 145 | 20 | 600 | 58 | 13000 | #DIV/0! | #DIV/0!
|  | 11:30:am | 25 | 4 | 169 | 7.5 | 1.7 | 149 | 3 | 173 | 7.7 | 25 | 153 | 12 | 178 | 7.9 | 29 | 147 | 17 |  |  |  | #DIV/0! | #DIV/0!
|  | 1:30:pm | 27 | 4 | 174 | 7.6 | 1.5 | 153 | 2 | 178 | 7.8 | 27 | 158 | 10 | 182 | 8 | 27 | 150 | 15 |  |  |  | #DIV/0! | #DIV/0!
Monday | 2010-11-15 | 9:30:am | 24 | 4.4 | 166 | 7.3 | 2.3 | 133 | 3 | 170 | 7.5 | 18 | 130 | 13 | 173 | 7.7 | 21 | 127 | 16 | _ | 56 | 12500 | 28.125 | 91.3043
|  | 11:30:am | 27 | 4.2 | 170 | 7.4 | 1.9 | 130 | 2 | 176 | 7.6 | 15 | 127 | 10 | 177 | 7.8 | 18 | 123 | 13 |  |  |  | 13.7931 | 93.2
|  | 1:30:pm | 29 | 4 | 175 | 7.5 | 1.4 | 127 | 1 | 180 | 7.7 | 13 | 124 | 9 | 183 | 7.9 | 15 | 120 | 10 |  |  |  | 0 | 94.4444
Tuesday | 2010-11-16 | 9:30:am | 24 | 4.2 | 156 | 7.4 | 2.2 | 139 | 2 | 159 | 7.5 | 14 | 135 | 7 | 162 | 7.6 | 19 | 133 | 9 | _ | 58 | 13000 | 14.2857 | 87.2222
|  | 11:30:am | 27 | 4 | 158 | 7.5 | 1.7 | 144 | 1 | 162 | 7.6 | 12 | 139 | 5 | 166 | 7.7 | 17 | 135 | 7 |  |  |  | 16.6667 | 87.3333
|  | 1:30:pm | 30 | 4 | 160 | 7.6 | 1.4 | 146 | 1 | 166 | 7.7 | 11 | 142 | 3 | 169 | 7.8 | 15 | 138 | 5 |  |  |  | 13.3333 | 89.2308
Wednesday | 2010-11-17 | 9:30:am | 22 | 4.5 | 158 | 7.3 | 2 | 134 | 2.4 | 160 | 7.5 | 16 | 130 | 6 | 163 | 7.7 | 23 | 128 | 10 | _ | 59 | 12500 | 26.3158 | 84.2857
|  | 11:30:am | 24 | 4.2 | 162 | 7.4 | 1.6 | 137 | 2 | 165 | 7.6 | 14 | 134 | 4 | 168 | 7.8 | 19 | 131 | 8 |  |  |  | 29.4118 | 85.8333
|  | 1:30:pm | 28 | 4 | 165 | 7.5 | 1.2 | 140 | 1.5 | 168 | 7.7 | 12 | 137 | 2 | 170 | 7.9 | 17 | 135 | 6 |  |  |  | 26.6667 | 87.2727
Thursday | 2010-11-18 | 9:30:am | 24 | 4 | 155 | 7.2 | 1.9 | 154 | 1 | 158 | 7.4 | 18 | 151 | 5 | 161 | 7.6 | 25 | 148 | 13 | _ | 57 | 13000 | 30.4348 | 87.5
|  | 11:30:am | 26 | 4 | 158 | 7.3 | 1.5 | 158 | 1 | 161 | 7.5 | 15 | 155 | 3 | 163 | 7.7 | 22 | 151 | 4 |  |  |  | 26.3158 | 88.5714
|  | 1:30:pm | 28 | 4 | 162 | 7.4 | 1 | 162 | 1 | 165 | 7.6 | 13 | 158 | 2 | 167 | 7.8 | 20 | 155 | 3 |  |  |  | 29.4118 | 90
Friday | 2010-11-19 | 9:30:am | 21 | 4.2 | 159 | 7.3 | 1.7 | 146 | 1.6 | 163 | 7.4 | 16 | 142 | 6 | 166 | 7.5 | 23 | 140 | 13 | _ | 58 | 13000 | 28 | 89.4444
|  | 11:30:am | 23 | 4 | 163 | 7.4 | 1.5 | 149 | 1.2 | 166 | 7.5 | 13 | 144 | 4 | 169 | 7.6 | 20 | 142 | 11 |  |  |  | 31.8182 | 90
|  | 1:30:pm | 26 | 4.2 | 166 | 7.5 | 1.3 | 152 | 1 | 169 | 7.6 | 11 | 148 | 3 | 171 | 7.7 | 18 | 144 | 9 |  |  |  | 35 | 92.3077
Saturday | 2010-11-20 | 9:30:am | 18 | 4.3 | 200 | 7.3 | 2.5 | 207 | 13 | 207 | 7.5 | 17 | 202 | 11 | 212 | 7.7 | 23 | 199 | 12 | _ | 59 | 13000 | 30.4348 | 89.375
|  | 11:30:am | 20 | 4.2 | 195 | 7.4 | 2.2 | 200 | 11 | 203 | 7.6 | 13 | 197 | 9 | 208 | 7.8 | 20 | 193 | 10 |  |  |  | 35 | 88.4615
|  | 1:30:pm | 22 | 4 | 190 | 7.5 | 1.8 | 197 | 9 | 197 | 7.7 | 11 | 193 | 7 | 200 | 7.9 | 17 | 190 | 8 |  |  |  | 38.8889 | 88.1818
Sunday | 2010-11-21 | 9:30:am | 16 | 4.4 | 210 | 7.4 | 2.4 | 215 | 7 | 214 | 7.6 | 19 | 210 | 12 | 218 | 7.8 | 25 | 206 | 13 | _ | 57 | 13000 | 26.087 | 85.2941
|  | 11:30:am | 19 | 4.1 | 205 | 7.5 | 2 | 210 | 5 | 208 | 7.7 | 14 | 205 | 8 | 213 | 7.9 | 22 | 201 | 9 |  |  |  | 35 | 83.0769
|  | 1:30:pm | 22 | 4 | 200 | 7.6 | 1.6 | 204 | 3 | 207 | 7.8 | 12 | 200 | 5 | 210 | 8 | 20 | 197 | 7 |  |  |  | 35.2941 | 83.6364
Monday | 2010-11-22 | 9:30:am | 17 | 4 | 188 | 7.5 | 2 | 222 | 6 | 196 | 7.6 | 21 | 218 | 14 | 203 | 7.8 | 29 | 211 | 12 | _ | 50 | 10000 | 24 | 87.3684
|  | 11:30:am | 19 | 4 | 193 | 7.6 | 1.8 | 218 | 4 | 199 | 7.7 | 18 | 213 | 11 | 201 | 7.9 | 25 | 208 | 11 |  |  |  | 36.3636 | 85.7143
|  | 1:30:pm | 22 | 4 | 198 | 7.7 | 1.5 | 211 | 2 | 203 | 7.8 | 15 | 209 | 10 | 205 | 8 | 22 | 204 | 9 |  |  |  | 40 | 86.6667
Tuesday | 2010-11-23 | 9:30:am | 18 | 4.6 | 202 | 7.3 | 1.9 | 234 | 7 | 207 | 7.5 | 16 | 230 | 9 | 211 | 7.7 | 23 | 226 | 14 | _ | 59 | 13000 | 27.5862 | 90.4762
|  | 11:30:am | 22 | 4.3 | 197 | 7.4 | 1.5 | 230 | 5 | 203 | 7.6 | 13 | 226 | 7 | 208 | 7.8 | 19 | 222 | 11 |  |  |  | 28 | 90
|  | 1:30:pm | 25 | 4 | 193 | 7.5 | 1.3 | 223 | 4 | 196 | 7.7 | 11 | 220 | 5 | 200 | 7.9 | 17 | 217 | 10 |  |  |  | 31.8182 | 90
Wednesday | 2010-11-24 | 9:30:am | 16 | 4.5 | 179 | 7.4 | 2.7 | 213 | 5 | 185 | 7.6 | 18 | 209 | 6 | 194 | 7.8 | 24 | 206 | 12 | _ | 57 | 13000 | 30.4348 | 88.125
|  | 11:30:am | 18 | 4.3 | 182 | 7.5 | 2.3 | 208 | 3 | 189 | 7.7 | 15 | 200 | 4 | 198 | 7.9 | 21 | 197 | 10 |  |  |  | 31.5789 | 88.4615
|  | 1:30:pm | 21 | 4 | 185 | 7.6 | 2 | 200 | 1 | 194 | 7.8 | 12 | 196 | 2 | 199 | 8 | 17 | 192 | 8 |  |  |  | 35.2941 | 88.1818
Thursday | 2010-11-25 | 9:30:am | 17 | 4.3 | 211 | 7.3 | 2.2 | 224 | 3 | 215 | 7.5 | 16 | 221 | 9 | 218 | 7.7 | 23 | 218 | 13 | _ | 55 | 12500 | 25 | 85
|  | 11:30:am | 19 | 4 | 218 | 7.4 | 1.9 | 227 | 2 | 220 | 7.6 | 14 | 225 | 7 | 223 | 7.8 | 21 | 221 | 11 |  |  |  | 28.5714 | 84.6667
|  | 1:30:pm | 23 | 4 | 222 | 7.5 | 1.4 | 230 | 1 | 224 | 7.7 | 11 | 228 | 6 | 228 | 8 | 19 | 225 | 9 |  |  |  | 29.4118 | 83.3333
Friday | 2010-11-26 | 9:30:am | 15 | 4.4 | 215 | 7.4 | 2 | 222 | 2 | 218 | 7.6 | 13 | 220 | 10 | 222 | 7.7 | 23 | 217 | 14 | _ | 59 | 12500 | 30.4348 | 86.25
|  | 11:30:am | 18 | 4.2 | 219 | 7.5 | 1.7 | 226 | 1 | 221 | 7.7 | 10 | 222 | 7 | 226 | 7.8 | 20 | 220 | 12 |  |  |  | 33.3333 | 86.4286
|  | 1:30:pm | 21 | 4 | 229 | 7.6 | 1.3 | 228 | 1 | 231 | 7.8 | 9 | 226 | 5 | 233 | 7.9 | 15 | 223 | 10 |  |  |  | 42.1053 | 87.2727
Saturday | 2010-11-27 | 9:30:am | 19 | 4.6 | 222 | 7.5 | 2.6 | 220 | 3 | 226 | 7.6 | 15 | 218 | 11 | 228 | 7.8 | 19 | 215 | 12 | _ | 58 | 13000 | 43.4783 | 84.6154
|  | 11:30:am | 22 | 4.3 | 227 | 7.6 | 2.3 | 223 | 1 | 230 | 7.7 | 11 | 221 | 9 | 232 | 7.9 | 17 | 218 | 10 |  |  |  | 50 | 83
|  | 1:30:pm | 24 | 4 | 231 | 7.7 | 2 | 225 | 1 | 234 | 7.8 | 10 | 223 | 7 | 237 | 7.9 | 15 | 221 | 8 |  |  |  | 40 | 85.5556
Sunday | 2010-11-28 | 9:30:am | 16 | 4.2 | 228 | 7.2 | 1.9 | 221 | 4 | 231 | 7.4 | 14 | 217 | 10 | 235 | 7.6 | 18 | 214 | 15 | _ | 59 | 12500 | 21.0526 | 82.6667
|  | 11:30:am | 18 | 4 | 231 | 7.4 | 1.5 | 226 | 3 | 234 | 7.5 | 11 | 222 | 8 | 238 | 7.7 | 15 | 218 | 11 |  |  |  | 35.2941 | 79.0909
|  | 1:30:pm | 20 | 4 | 235 | 7.5 | 1.2 | 229 | 2 | 238 | 7.6 | 9 | 227 | 6 | 242 | 7.8 | 12 | 222 | 9 |  |  |  | 33.3333 | 80
Monday | 2010-11-29 | 9:30:am | 15 | 4 | 225 | 7.3 | 1.6 | 231 | 2 | 227 | 7.4 | 12 | 227 | 9 | 231 | 7.6 | 15 | 223 | 9 | _ | 57 | 12500 | 22.2222 | 86.4286
|  | 11:30:am | 18 | 4 | 229 | 7.4 | 1 | 235 | 1 | 231 | 7.6 | 9 | 232 | 7 | 235 | 7.7 | 13 | 227 | 7 |  |  |  | 26.6667 | 86.3636
|  | 1:30:pm | 23 | 4 | 235 | 7.5 | 0.8 | 238 | 1 | 237 | 7.7 | 7 | 236 | 5 | 239 | 7.8 | 12 | 232 | 5 |  |  |  | 25 | 86.6667
Tuesday | 2010-11-30 | 9:30:am | [20 empty] | 20 | 86.6667 | bar: EC to PH; TDS to AFTER SEDIMENTATION PH; AFTER SEDIMENTATION TDS to RAW (INLET WATER) PH; RAW (INLET WATER) TDS to RAW (INLET WATER) TSS
|  | 11:30:am | [20 empty] | 30.7692 | 88.8889 | bar: EC to PH; TDS to AFTER SEDIMENTATION PH; AFTER SEDIMENTATION TDS to RAW (INLET WATER) PH; RAW (INLET WATER) TDS to RAW (INLET WATER) TSS
|  | 1:30:pm | [20 empty] | 41.6667 | 88.5714 | bar: EC to PH; TDS to AFTER SEDIMENTATION PH; AFTER SEDIMENTATION TDS to RAW (INLET WATER) PH; RAW (INLET WATER) TDS to RAW (INLET WATER) TSS

## 12
Subject | CHEMICAL TEST RESULTS
Location | KIRKUK UNIFIED WATER PLANT ( KUWP )
Date | 2010-12-01
DAYS | DATE | TIME | TEMP | SUPPLY(OUTLET WATER) | [5 empty] | AFTER SEDIMENTATION |  |  |  |  | RAW (INLET WATER) |  |  |  |  | ALUM Kg/D | CL2 Kg/h | FLOW (m3/hr)
|  |  |  | CL2 | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS | EC | PH | TU | TDS | TSS |  |  |  | S-R | S-SUP
Tuesday | 2010-12-01 | 9:30:am | 14 | 4.2 | 266 | 7.3 | 2.2 | 310 | 3 | 269 | 7.5 | 12 | 300 | 4 | 272 | 7.7 | 16 | 294 | 8 | _ | 54 | 12500 | 25 | 81.6667
|  | 11:30:am | 16 | 4 | 260 | 7.4 | 1.9 | 300 | 2 | 266 | 7.6 | 10 | 295 | 2 | 269 | 7.8 | 12 | 287 | 6 |  |  |  | 16.6667 | 81
|  | 1:30:pm | 18 | 4 | 255 | 7.5 | 1.6 | 295 | 1 | 261 | 7.7 | 8 | 288 | 2 | 263 | 7.9 | 11 | 283 | 5 |  |  |  | 27.2727 | 80
Wednesday | 2010-12-02 | 9:30:am | 15 | 4.4 | 233 | 7.4 | 1.9 | 299 | 3 | 237 | 7.6 | 12 | 291 | 6 | 240 | 7.7 | 19 | 288 | 5 | _ | 58 | 13000 | 36.8421 | 84.1667
|  | 11:30:am | 18 | 4.2 | 237 | 7.5 | 1.6 | 289 | 1 | 240 | 7.7 | 10 | 283 | 4 | 244 | 7.8 | 15 | 280 | 3 |  |  |  | 33.3333 | 84
|  | 1:30:pm | 21 | 4 | 242 | 7.6 | 1.2 | 288 | 1 | 245 | 7.8 | 8 | 278 | 3 | 248 | 7.9 | 13 | 276 | 2 |  |  |  | 38.4615 | 85
Thursday | 2010-12-03 | 9:30:am | 16 | 4.4 | 222 | 7.5 | 2 | 264 | 3 | 227 | 7.6 | 11 | 260 | 7 | 232 | 7.8 | 15 | 256 | 8 | _ | 59 | 13000 | 26.6667 | 81.8182
|  | 11:30:am | 19 | 4.2 | 227 | 7.6 | 1.7 | 260 | 2 | 231 | 7.7 | 9 | 255 | 5 | 236 | 7.9 | 13 | 251 | 6 |  |  |  | 30.7692 | 81.1111
|  | 1:30:pm | 22 | 4 | 231 | 7.7 | 1.4 | 255 | 1 | 234 | 7.8 | 7 | 250 | 3 | 238 | 8 | 11 | 248 | 5 |  |  |  | 36.3636 | 80
Friday | 2010-12-04 | 9:30:am | 16 | 4.2 | 218 | 7.3 | 1.9 | 215 | 3 | 222 | 7.5 | 17 | 211 | 9 | 226 | 7.6 | 23 | 206 | 12 | _ | 56 | 12500 | 26.087 | 88.8235
|  | 11:30:am | 20 | 4 | 222 | 7.4 | 1.6 | 211 | 3 | 227 | 7.6 | 12 | 207 | 7 | 229 | 7.7 | 19 | 202 | 10 |  |  |  | 36.8421 | 86.6667
|  | 1:30:pm | 24 | 4 | 225 | 7.5 | 1.2 | 208 | 2 | 229 | 7.7 | 11 | 203 | 6 | 232 | 7.8 | 15 | 200 | 8 |  |  |  | 26.6667 | 89.0909
Saturday | 2010-12-05 | 9:30:am | 13 | 4 | 211 | 7.5 | 1.6 | 206 | 2 | 215 | 7.7 | 13 | 200 | 7 | 218 | 7.8 | 17 | 197 | 10 | _ | 58 | 13000 | 23.5294 | 87.6923
|  | 11:30:am | 15 | 4 | 208 | 7.6 | 1.3 | 200 | 1 | 212 | 7.8 | 11 | 196 | 5 | 216 | 7.9 | 15 | 192 | 7 |  |  |  | 26.6667 | 88.1818
|  | 1:30:pm | 18 | 4 | 204 | 7.7 | 1 | 197 | 1 | 208 | 7.9 | 10 | 194 | 4 | 211 | 8 | 14 | 188 | 6 |  |  |  | 28.5714 | 90
Sunday | 2010-12-06 | 9:30:am | 16 | 4.3 | 210 | 7.4 | 2.3 | 200 | 3 | 213 | 7.6 | 15 | 197 | 10 | 216 | 7.8 | 19 | 193 | 12 | _ | 56 | 13000 | 21.0526 | 84.6667
|  | 11:30:am | 19 | 4 | 205 | 7.5 | 2 | 194 | 2 | 208 | 7.7 | 12 | 190 | 8 | 212 | 7.9 | 16 | 188 | 10 |  |  |  | 25 | 83.3333
|  | 1:30:pm | 22 | 4 | 199 | 7.6 | 1.7 | 190 | 1 | 203 | 7.8 | 11 | 187 | 7 | 208 | 8 | 14 | 183 | 9 |  |  |  | 21.4286 | 84.5455
Monday | 2010-12-07 | 9:30:am | 12 | 4.4 | 199 | 7.3 | 2.2 | 211 | 3 | 203 | 7.5 | 15 | 207 | 7 | 207 | 7.7 | 22 | 202 | 11 | _ | 59 | 13000 | 31.8182 | 85.3333
|  | 11:30:am | 15 | 4.2 | 194 | 7.4 | 1.8 | 200 | 2 | 200 | 7.6 | 17 | 197 | 5 | 203 | 7.8 | 19 | 194 | 9 |  |  |  | 10.5263 | 89.4118
|  | 1:30:pm | 18 | 4 | 192 | 7.5 | 1.6 | 199 | 1 | 196 | 7.7 | 16 | 192 | 3 | 199 | 7.9 | 17 | 188 | 7 |  |  |  | 5.8824 | 90
Tuesday | 2010-12-08 | 9:30:am | 13 | 4.5 | 210 | 7.5 | 2.4 | 206 | 2 | 214 | 7.7 | 13 | 199 | 8 | 219 | 7.8 | 25 | 194 | 14 | _ | 58 | 12500 | 48 | 81.5385
|  | 11:30:am | 17 | 4.2 | 203 | 7.6 | 2.2 | 200 | 1 | 209 | 7.8 | 16 | 192 | 6 | 213 | 7.9 | 22 | 188 | 12 |  |  |  | 27.2727 | 86.25
|  | 1:30:pm | 20 | 4 | 200 | 7.7 | 1.8 | 197 | 1 | 203 | 7.8 | 18 | 187 | 4 | 207 | 8 | 20 | 182 | 10 |  |  |  | 10 | 90
Wednesday | 2010-12-09 | 9:30:am | 11 | 4.3 | 195 | 7.4 | 2 | 199 | 4 | 201 | 7.6 | 16 | 192 | 5 | 209 | 7.8 | 26 | 188 | 14 | _ | 57 | 12500 | 38.4615 | 87.5
|  | 11:30:am | 14 | 4 | 192 | 7.6 | 1.7 | 195 | 3 | 197 | 7.7 | 18 | 187 | 3 | 202 | 7.9 | 23 | 182 | 13 |  |  |  | 21.7391 | 90.5556
|  | 1:30:pm | 18 | 4 | 190 | 7.6 | 1.3 | 190 | 2 | 192 | 7.8 | 20 | 183 | 2 | 197 | 8 | 24 | 178 | 11 |  |  |  | 16.6667 | 93.5
Thursday | 2010-12-10 | 9:30:am | 14 | 4.4 | 200 | 7.3 | 1.8 | 195 | 3 | 208 | 7.5 | 11 | 192 | 9 | 214 | 7.7 | 23 | 188 | 17 | _ | 59 | 12500 | 52.1739 | 83.6364
|  | 11:30:am | 16 | 4.2 | 210 | 7.4 | 1.5 | 190 | 2 | 216 | 7.6 | 15 | 188 | 7 | 223 | 7.8 | 20 | 181 | 13 |  |  |  | 25 | 90
|  | 1:30:pm | 19 | 4 | 213 | 7.5 | 1.2 | 188 | 1 | 220 | 7.7 | 17 | 183 | 6 | 228 | 7.9 | 23 | 178 | 11 |  |  |  | 26.087 | 92.9412
Friday | 2010-12-11 | 9:30:am | 14 | 4.6 | 215 | 7.4 | 2 | 221 | 3 | 218 | 7.6 | 19 | 217 | 13 | 222 | 7.7 | 26 | 213 | 16 | _ | 57 | 13000 | 26.9231 | 89.4737
|  | 11:30:am | 16 | 4.2 | 209 | 7.5 | 1.8 | 218 | 2 | 213 | 7.7 | 17 | 213 | 10 | 219 | 7.8 | 23 | 210 | 12 |  |  |  | 26.087 | 89.4118
|  | 1:30:pm | 19 | 4 | 203 | 7.7 | 1.4 | 215 | 1 | 208 | 7.8 | 13 | 208 | 7 | 213 | 7.9 | 21 | 205 | 10 |  |  |  | 38.0952 | 89.2308
Saturday | 2010-12-12 | 9:30:am | 12 | 4.3 | 221 | 7.3 | 1.8 | 213 | 4 | 224 | 7.5 | 17 | 210 | 14 | 229 | 7.7 | 23 | 207 | 15 | _ | 58 | 12500 | 26.087 | 89.4118
|  | 11:30:am | 14 | 4 | 224 | 7.4 | 1.5 | 210 | 2 | 227 | 7.6 | 14 | 207 | 12 | 231 | 7.8 | 21 | 202 | 11 |  |  |  | 33.3333 | 89.2857
|  | 1:30:pm | 17 | 4 | 227 | 7.5 | 1.2 | 208 | 1 | 231 | 7.7 | 12 | 202 | 9 | 235 | 7.9 | 19 | 197 | 8 |  |  |  | 36.8421 | 90
Sunday | 2010-12-13 | 9:30:am | 13 | 4.5 | 218 | 7.5 | 2 | 217 | 5 | 222 | 7.6 | 19 | 212 | 13 | 226 | 7.8 | 25 | 207 | 17 | _ | 55 | 13000 | 24 | 89.4737
|  | 11:30:am | 15 | 4.2 | 213 | 7.6 | 1.7 | 213 | 3 | 218 | 7.7 | 16 | 208 | 10 | 222 | 7.9 | 22 | 202 | 12 |  |  |  | 27.2727 | 89.375
|  | 1:30:pm | 17 | 4 | 209 | 7.7 | 1.3 | 210 | 2 | 214 | 7.8 | 12 | 203 | 7 | 218 | 8 | 19 | 199 | 10 |  |  |  | 36.8421 | 89.1667
Monday | 2010-12-14 | 9:30:am | 16 | 4.6 | 214 | 7.2 | 1.8 | 210 | 3 | 218 | 7.4 | 18 | 207 | 11 | 223 | 7.6 | 22 | 202 | 18 | _ | 58 | 13000 | 18.1818 | 90
|  | 11:30:am | 18 | 4.3 | 218 | 7.3 | 1.5 | 208 | 2 | 222 | 7.5 | 15 | 202 | 8 | 226 | 7.7 | 20 | 197 | 15 |  |  |  | 25 | 90
|  | 1:30:pm | 20 | 4 | 221 | 7.4 | 1.2 | 202 | 1 | 227 | 7.6 | 12 | 200 | 6 | 231 | 7.8 | 17 | 192 | 12 |  |  |  | 29.4118 | 90
Tuesday | 2010-12-15 | 9:30:am | 12 | 4.5 | 223 | 7.4 | 2.4 | 219 | 3 | 227 | 7.6 | 15 | 214 | 13 | 231 | 7.8 | 26 | 210 | 14 | _ | 56 | 12500 | 42.3077 | 84
|  | 11:30:am | 14 | 4.3 | 227 | 7.5 | 2 | 213 | 1 | 231 | 7.7 | 12 | 210 | 10 | 235 | 7.9 | 23 | 206 | 10 |  |  |  | 47.8261 | 83.3333
|  | 1:30:pm | 16 | 4 | 229 | 7.6 | 1.8 | 210 | 1 | 235 | 7.8 | 11 | 206 | 7 | 239 | 8 | 21 | 200 | 7 |  |  |  | 47.619 | 83.6364
Wednesday | 2010-12-16 | 9:30:am | 15 | 4.2 | 222 | 7.5 | 2 | 222 | 2 | 225 | 7.7 | 16 | 221 | 12 | 229 | 7.9 | 27 | 218 | 13 | _ | 58 | 13000 | 40.7407 | 87.5
|  | 11:30:am | 17 | 4 | 225 | 7.6 | 1.7 | 218 | 1 | 229 | 7.7 | 13 | 216 | 7 | 234 | 8 | 24 | 213 | 11 |  |  |  | 45.8333 | 86.9231
|  | 1:30:pm | 19 | 4 | 229 | 7.7 | 1.2 | 213 | 1 | 232 | 7.8 | 11 | 210 | 5 | 237 | 8 | 22 | 207 | 9 |  |  |  | 50 | 89.0909
Thursday | 2010-12-17 | 9:30:am | 14 | 4.4 | 218 | 7.3 | 1.7 | 222 | 4 | 222 | 7.5 | 15 | 217 | 13 | 228 | 7.7 | 25 | 212 | 14 | _ | 59 | 12500 | 40 | 88.6667
|  | 11:30:am | 16 | 4.2 | 222 | 7.5 | 1.5 | 217 | 3 | 226 | 7.6 | 12 | 212 | 10 | 233 | 7.8 | 21 | 208 | 11 |  |  |  | 42.8571 | 87.5
|  | 1:30:pm | 19 | 4 | 229 | 7.6 | 1.2 | 208 | 2 | 231 | 7.7 | 10 | 206 | 6 | 237 | 7.9 | 18 | 202 | 10 |  |  |  | 44.4444 | 88
Friday | 2010-12-18 | 9:30:am | 12 | 4.3 | 211 | 7.3 | 3.6 | 221 | 6 | 208 | 7.5 | 23 | 218 | 18 | 203 | 7.7 | 39 | 214 | 23 | 2250 | 57 | 13000 | 41.0256 | 84.3478
|  | 11:30:am | 14 | 4 | 207 | 7.4 | 3 | 228 | 4 | 203 | 7.6 | 27 | 222 | 15 | 200 | 7.8 | 35 | 217 | 20 |  |  |  | 22.8571 | 88.8889
|  | 1:30:pm | 16 | 4 | 203 | 7.5 | 2.8 | 232 | 3 | 200 | 7.7 | 29 | 227 | 12 | 199 | 7.9 | 33 | 221 | 17 |  |  |  | 12.1212 | 90.3448
Saturday | 2010-12-19 | 9:30:am | 11 | 4.2 | 216 | 7.4 | 3.5 | 225 | 7 | 211 | 7.6 | 28 | 221 | 23 | 207 | 7.8 | 40 | 218 | 29 | 1050 | 58 | 13000 | 30 | 87.5
|  | 11:30:am | 14 | 4 | 211 | 7.5 | 3.2 | 229 | 5 | 207 | 7.7 | 26 | 225 | 21 | 203 | 7.9 | 35 | 222 | 24 |  |  |  | 25.7143 | 87.6923
|  | 1:30:pm | 16 | 4 | 207 | 7.6 | 2.9 | 234 | 3 | 202 | 7.8 | 22 | 230 | 18 | 200 | 8 | 32 | 225 | 22 |  |  |  | 31.25 | 86.8182
Sunday | 2010-12-20 | 9:30:am | 15 | 4.6 | 219 | 7.3 | 3 | 229 | 5 | 214 | 7.5 | 29 | 222 | 22 | 211 | 7.7 | 39 | 220 | 29 | 1050 | 59 | 13000 | 25.641 | 89.6552
|  | 11:30:am | 16 | 4.3 | 215 | 7.5 | 2.8 | 234 | 3 | 210 | 7.6 | 25 | 228 | 19 | 208 | 7.8 | 36 | 223 | 23 |  |  |  | 30.5556 | 88.8
|  | 1:30:pm | 18 | 4 | 213 | 7.6 | 2.5 | 239 | 2 | 207 | 7.7 | 23 | 234 | 17 | 203 | 7.9 | 33 | 229 | 21 |  |  |  | 30.303 | 89.1304
Monday | 2010-12-21 | 9:30:am | 13 | 4.5 | 228 | 7.2 | 2.7 | 231 | 7 | 221 | 7.4 | 31 | 226 | 25 | 218 | 7.6 | 43 | 221 | 31 | 1050 | 57 | 13000 | 27.907 | 91.2903
|  | 11:30:am | 16 | 4.2 | 222 | 7.3 | 2.2 | 238 | 5 | 217 | 7.5 | 30 | 230 | 23 | 214 | 7.7 | 39 | 227 | 28 |  |  |  | 23.0769 | 92.6667
|  | 1:30:pm | 19 | 4 | 220 | 7.4 | 2 | 243 | 3 | 215 | 7.6 | 28 | 235 | 21 | 211 | 7.8 | 36 | 230 | 25 |  |  |  | 22.2222 | 92.8571
Tuesday | 2010-12-22 | 9:30:am | 15 | 4.4 | 231 | 7.5 | 2.5 | 229 | 4 | 227 | 7.6 | 21 | 223 | 17 | 223 | 7.7 | 29 | 220 | 23 | _ | 50 | 10000 | 27.5862 | 88.0952
|  | 11:30:am | 16 | 4.2 | 228 | 7.6 | 2.3 | 232 | 2 | 225 | 7.7 | 19 | 227 | 13 | 219 | 7.8 | 26 | 223 | 21 |  |  |  | 26.9231 | 87.8947
|  | 1:30:pm | 18 | 4 | 223 | 7.7 | 2 | 236 | 1 | 220 | 7.8 | 17 | 232 | 11 | 215 | 7.9 | 23 | 228 | 18 |  |  |  | 26.087 | 88.2353
Wednesday | 2010-12-23 | 9:30:am | 16 | 4.3 | 213 | 7.3 | 1.8 | 228 | 3 | 210 | 7.5 | 15 | 222 | 10 | 208 | 7.6 | 24 | 220 | 17 | _ | 59 | 13000 | 37.5 | 88
|  | 11:30:am | 18 | 4 | 220 | 7.4 | 1.5 | 222 | 2 | 223 | 7.6 | 17 | 217 | 7 | 226 | 7.7 | 27 | 211 | 13 |  |  |  | 37.037 | 91.1765
|  | 1:30:pm | 21 | 4 | 222 | 7.5 | 1.3 | 218 | 1 | 225 | 7.7 | 19 | 211 | 5 | 229 | 7.8 | 29 | 208 | 11 |  |  |  | 34.4828 | 93.1579
Thursday | 2010-12-24 | 9:30:am | 13 | 4.3 | 208 | 7.4 | 1.7 | 199 | 3 | 213 | 7.6 | 18 | 193 | 11 | 216 | 7.7 | 27 | 190 | 12 | _ | 57 | 13000 | 33.3333 | 90.5556
|  | 11:30:am | 16 | 4 | 202 | 7.5 | 1.3 | 192 | 2 | 209 | 7.7 | 23 | 190 | 9 | 211 | 7.8 | 29 | 184 | 11 |  |  |  | 20.6897 | 94.3478
|  | 1:30:pm | 19 | 4 | 199 | 7.6 | 1 | 188 | 2 | 205 | 7.8 | 28 | 185 | 7 | 208 | 7.9 | 31 | 180 | 9 |  |  |  | 9.6774 | 96.4286
Friday | 2010-12-25 | 9:30:am | 12 | 4.2 | 222 | 7.3 | 1.3 | 194 | 4 | 217 | 7.4 | 15 | 190 | 8 | 222 | 7.6 | 22 | 188 | 10 | _ | 55 | 12500 | 31.8182 | 91.3333
|  | 11:30:am | 15 | 4 | 218 | 7.4 | 1 | 190 | 3 | 211 | 7.5 | 18 | 185 | 6 | 218 | 7.7 | 24 | 182 | 8 |  |  |  | 25 | 94.4444
|  | 1:30:pm | 18 | 4 | 214 | 7.5 | 1 | 188 | 1 | 207 | 7.6 | 23 | 180 | 4 | 211 | 7.8 | 27 | 178 | 7 |  |  |  | 14.8148 | 95.6522
Saturday | 2010-12-26 | 9:30:am | 16 | 4.4 | 211 | 7.4 | 1.2 | 195 | 2 | 213 | 7.6 | 18 | 190 | 12 | 213 | 7.8 | 24 | 185 | 13 | _ | 59 | 12500 | 25 | 93.3333
|  | 11:30:am | 18 | 4.2 | 215 | 7.5 | 1 | 190 | 1 | 218 | 7.7 | 15 | 187 | 10 | 222 | 7.9 | 22 | 180 | 10 |  |  |  | 31.8182 | 93.3333
|  | 1:30:pm | 21 | 4 | 220 | 7.6 | 0.8 | 188 | 1 | 222 | 7.8 | 14 | 182 | 8 | 227 | 8 | 20 | 178 | 9 |  |  |  | 30 | 94.2857
Sunday | 2010-12-27 | 9:30:am | 17 | 4.6 | 215 | 7.5 | 2 | 212 | 3 | 218 | 7.6 | 17 | 208 | 12 | 222 | 7.7 | 28 | 205 | 17 | _ | 58 | 13000 | 39.2857 | 88.2353
|  | 11:30:am | 20 | 4.3 | 220 | 7.6 | 1.6 | 215 | 2 | 224 | 7.7 | 20 | 212 | 10 | 228 | 7.8 | 25 | 209 | 13 |  |  |  | 20 | 92
|  | 1:30:pm | 23 | 4 | 225 | 7.6 | 1.3 | 219 | 1 | 229 | 7.7 | 21 | 218 | 7 | 231 | 7.9 | 26 | 213 | 11 |  |  |  | 19.2308 | 93.8095
Monday | 2010-12-28 | 9:30:am | 15 | 4.3 | 222 | 7.4 | 2.5 | 222 | 3 | 227 | 7.6 | 17 | 217 | 11 | 232 | 7.8 | 22 | 212 | 16 | _ | 59 | 12500 | 22.7273 | 85.2941
|  | 11:30:am | 18 | 4 | 220 | 7.5 | 2 | 219 | 2 | 225 | 7.7 | 19 | 214 | 9 | 229 | 7.9 | 26 | 210 | 13 |  |  |  | 26.9231 | 89.4737
|  | 1:30:pm | 21 | 4 | 217 | 7.6 | 1.7 | 214 | 1 | 223 | 7.8 | 21 | 211 | 7 | 225 | 8 | 29 | 207 | 10 |  |  |  | 27.5862 | 91.9048
Tuesday | 2010-12-29 | 9:30:am | 13 | 4.4 | 224 | 7.5 | 2 | 211 | 2 | 228 | 7.6 | 18 | 208 | 11 | 232 | 7.7 | 24 | 203 | 17 | _ | 57 | 12500 | 25 | 88.8889
|  | 11:30:am | 16 | 4.2 | 220 | 7.6 | 1.7 | 206 | 1 | 224 | 7.7 | 19 | 202 | 8 | 228 | 7.8 | 22 | 200 | 15 |  |  |  | 13.6364 | 91.0526
|  | 1:30:pm | 18 | 4 | 218 | 7.7 | 1.4 | 200 | 1 | 220 | 7.8 | 21 | 196 | 6 | 223 | 7.9 | 24 | 194 | 12 |  |  |  | 12.5 | 93.3333
Wednesday | 2010-12-30 | 9:30:am | 12 | 4.3 | 229 | 7.4 | 1.9 | 206 | 3 | 234 | 7.5 | 15 | 202 | 10 | 238 | 7.7 | 20 | 200 | 16 | _ | 60 | 12500 | 25 | 87.3333
|  | 11:30:am | 15 | 4 | 231 | 7.5 | 1.5 | 200 | 2 | 232 | 7.6 | 17 | 198 | 7 | 235 | 7.8 | 18 | 195 | 13 |  |  |  | 5.5556 | 91.1765
|  | 1:30:pm | 17 | 4 | 235 | 7.6 | 1.2 | 198 | 1 | 238 | 7.7 | 19 | 194 | 5 | 242 | 8 | 22 | 190 | 11 |  |  |  | 13.6364 | 93.6842
Thursday | 2010-12-31 | 9:30 | 15 | 4.5 | 226 | 7.3 | 1.7 | 202 | 1 | 229 | 7.4 | 13 | 199 | 9 | 233 | 7.5 | 21 | 194 | 15 | _ | 59 | 12500 | 38.0952 | 86.9231
|  | 11:30 | 19 | 4.2 | 229 | 7.4 | 1.4 | 199 | 1 | 235 | 7.5 | 11 | 195 | 6 | 238 | 7.6 | 20 | 190 | 13 |  |  |  | 45 | 87.2727
|  | 1:30:pm | 21 | 4 | 233 | 7.5 | 1 | 195 | 1 | 238 | 7.6 | 14 | 190 | 5 | 240 | 7.7 | 18 | 188 | 10 |  |  |  | 22.2222 | 92.8571